## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-TE-LI-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1045 |  |  | Transmital Date: Jun-07th-2022
Document Title: Cable Schedule For PABX System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-TE-TR-1045 |  |  | Transmital Date: Jun-07th-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-TE-LI-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به نامه 42940 ،با توجه به اینکه تجهیز PABX أر این پروژه موضوعیت ندارد ،به جای PABX عبارت TELECOM EQUIPMENT استفاده شود |  | 1401-2294-128504 | 1401/4/12 | تغییر یافت
2 | جهت شماره گذاری کابل بر اساس فرمت ارسالی نامه118236 مورخ 5/4/1401 استفاده شود |  | 128504 | 1401/4/12 | در نامه مذکور به نحوه نامگذاری کابلهای تله کام اشاره نشده است.در هر صورت از نام گذاری ساده و آسان استفاده شده است
3 | کلیه کابلهایی که از منظقه فرایندی عبو ر می نمایند بایستی دارای روکش سربی یاشند |  | 128504 | 1401/4/12 | اعمال گردید
4 | بر اساس مدارک پایه ، قطر کابلهای مخابراتی برای محیط های بیرون 0.8 mm و برای محیط های داخلی 0.6 mm میباشد |  | 128504 | 1401/4/12 | اعمال گردید
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: AP.Golrang | Signature |  |  |  | Clarified By: | Signature
| Date: Jun-25th-2022 |  |  |  |  | Date: