## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-TE-LI-0004_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1045 |  |  | Transmital Date: Jun-07th-2022
Document Title: Cable Schedule For PAGA System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-TE-TR-1045 |  |  | Transmital Date: Jun-07th-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-TE-LI-0004_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | کلیه کابلهایی که از منظقه فرایندی عبور می نمایند بایستی دارای روکش سربی یاشند. |  | 1401-2294-128504 | 1401-4-12 | اعمال گردید.
2 | جهت کابل سیستم از JB تا LOUD SPEAKER ا زکابل آرموردار استفاده شود. |  | 1401-2294-128504 | 1401-4-12 | طی شفاف سازی اخیر کابلهای مربوطه از داخل لوله بر روی پایه بلندگو عبور خواهند نمود و نیازی به آرمور نخواهد بود.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: AP.Golrang | Signature |  |  |  | Clarified By: | Signature
| Date: Jun-25th-2022 |  |  |  |  | Date: