## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 18
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0004 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST FOR F&G SYSTEMS نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | OCT.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAY.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number:F0Z-708970
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 18
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0004 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | X | [5 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | X | [5 empty] | 71
8 | X | X | X | [5 empty] | 72
9 |  | X | X | [5 empty] | 73
10 |  | X | X | [5 empty] | 74
11 |  | X | X | [5 empty] | 75
12 |  | X | X | [5 empty] | 76
13 |  | X | X | [5 empty] | 77
14 |  | X | X | [5 empty] | 78
15 |  |  | X | [5 empty] | 79
16 |  |  | X | [5 empty] | 80
17 |  |  | X | [5 empty] | 81
18 |  |  | X | [5 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 18
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0004 | D02
REFERENCES(NOTE 2):
| F&G LOCATION LAYOUT FOR PROCESS Area | [7 empty] | BK-GCS-PEDCO-120-IN-PY-0005
| F&G LOCATION LAYOUT FOR BUILDINGS | [7 empty] | BK-GCS-PEDCO-120-IN-PY-0006
| DATA SHEET FOR MATRIX PANEL | [7 empty] | BK-GCS-PEDCO-120-IN-DT-0017
| ESD LEVEL HIERARCHY | [7 empty] | BK-GCS-PEDCO-120-IN-DG-0003
| FIRE & GAS DETECTION DESIGN CRITERIA | [7 empty] | BK-GCS-PEDCO-120-IN-DC-0001
GENERAL NOTE
| 1 | ALL LISTED FACP'S SIGNALS SHALL BE MONITORED IN F&G SYSTEM BY MODBUS CONNECTION.
| 2 | REFER TO LATEST VERSION OF REFERENCE DOCUMENTS.
| 3 | ALL RELAYS & I.S. BARRIERS INSTALLED IN F&G PANEL SHALL BE SIL CERTIFIED. ALL RELAYS SHALL BE LINE-MONITORED
| 4 | GALVANIC ISOLATION BARRIER SHALL BE CONSIDERED FOR INTRINSICALLY SAFE (EEXia) LOOPS.
| 5 | I/O CARDS & ACCESSORIES SHALL BE SELECTED IN ACCORDANCE WITH '' SPECIFICATION FOR CONTROL SYSTEM".

## SUMMARY
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: | [5 empty] | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 4 از 18
9184 – 073 - 053 | [5 empty] | BK | GCS |  | PEDCO | 120 | IN | LI | 0004 | D02
F&G I/O SUMMERY COUNT
| ITEM |  | I/O TYPE |  | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS |  | QTY (+20% SPARE) | REMARKS
| 1 |  | AI-IS-R |  | IS | R |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 88 |  | 106 | NOTES 4,5 | 105.6
| 2 |  | DI-NIS-R |  | NIS | R |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 47 |  | 57 |  | 56.4
| 3 |  | DO-NIS-R |  | NIS | R |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 130 |  | 156 |  | 156
ABBREVIATIONS:
|  | I/O |  | INPUT / OUTPUT | [7 empty] | DCS: | DISTRIBUTED CONTROL SYSTEM
|  | DI: |  | DIGITAL INPUT SIGNAL | [7 empty] | ESD: | EMERGENCY SHUT DOWN SYSTEM
|  | DO: |  | DIGITAL OUTPUT SIGNAL | [7 empty] | F&G | FIRE AND GAS CONTROL SYSTEM
|  | AI: |  | ANALOGUE INPUT SIGNAL | [7 empty] | MCC: | MOTOR CONTROL CENTER
|  | AO: |  | ANALOGUE OUTPUT SIGNAL | [7 empty] | IRP: | INTERPOSING RELAY PANEL
|  | IND: |  | INDICATION | [7 empty] | CH: | CHANNEL
|  | STA: |  | STATUS | [7 empty] | ADD: | ADDRESS
|  | COM: |  | COMMAND | [7 empty] | TB: | TERMINAL BLOCK
|  | IS: |  | INTRINSICALLY SAFE | [7 empty] | R: | REDUNDANT
|  | NIS: |  | NON INTRINSICALLY SAFE | [7 empty] | NR: | NON-REDUNDANT
|  | MAC: |  | MANUAL CALL POINT | [7 empty] | BR: | BLUE BEACON
|  | HN: |  | HORN | [7 empty] | BB: | RED BEACON
|  | LHD: |  | LINEAER HEAT DETECTOR | [7 empty] | FGD: | FLAMMABLE GAS DETECTOR
|  | SD: |  | SMOKE DETECTOR | [7 empty] | TGD: | TOXIC GAS DETECTOR
|  | BL: |  | BELL | [7 empty] | FD: | FLAME DETECTOR
|  | FACP: |  | FIRE ALARM CONTROL PANEL | [7 empty] | IRP: | INTERFACE RELAY PANEL
D02

## IO List for F&G System
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  |  | رشته |  | نوع مدرک | سریال |  |  | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO |  | 120 |  |  | IN |  | LI | 0004 |  |  | D02
SIGNALS TO F&G SYSTEM
ITEM | TAG | DESCRIPTION | LOCATION |  | P&ID |  | SIGNAL TYPE/ Area CLASSIFICATION | I/O TYPE |  | FROM |  | TO |  | JB NO. | POWER SUPPLY | Cable Type | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | I/O TYPE (ADDRE./CONV.) | REMARK | REV.
[17 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | HH | H | L | LL
FOR PROCESS AREA
1 | MAC-1001 | Manual Call Point | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
2 | MAC-1002 | Manual Call Point | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
3 | HN-1001 | Horn | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
4 | BR-1001 | Beacon - Red | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
5 | BB-1001 | Beacon - Blue | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
6 | BY-1001 | Beacon - Yellow | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
7 | MAC-2001 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
8 | MAC-2002 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
9 | MAC-2003 | Manual Call Point | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
10 | HN-2001 | Horn | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
11 | BR-2001 | Beacon - Red | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
12 | BB-2001 | Beacon - Blue | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
13 | BY-2001 | Beacon - Yellow | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
14 | MAC-3001 | Manual Call Point | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
15 | HN-3001 | Horn | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
16 | BR-3001 | Beacon - Red | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
17 | BB-3001 | Beacon - Blue | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
18 | BY-3001 | Beacon - Yellow | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
19 | MAC-4001 | Manual Call Point | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
20 | MAC-4002 | Manual Call Point | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
21 | HN-4001 | Horn | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 OF 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
22 | BR-4001 | Beacon - Red | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
23 | BB-4001 | Beacon - Blue | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
24 | BY-4001 | Beacon - Yellow | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
25 | HN-4002 | Horn | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
26 | BR-4002 | Beacon - Red | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
27 | BB-4002 | Beacon - Blue | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
28 | BY-4002 | Beacon - Yellow | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
29 | MAC-5001 | Manual Call Point | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
30 | MAC-5002 | Manual Call Point | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
31 | HN-5001 | Horn | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
32 | BR-5001 | Beacon - Red | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
33 | BB-5001 | Beacon - Blue | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
34 | BY-5001 | Beacon - Yellow | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
35 | MAC-6001 | Manual Call Point | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
36 | MAC-6002 | Manual Call Point | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
37 | HN-6001 | Horn | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
38 | BR-6001 | Beacon - Red | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
39 | BB-6001 | Beacon - Blue | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
40 | BY-6001 | Beacon - Yellow | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
41 | MAC-7001 | Manual Call Point | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
42 | MAC-7002 | Manual Call Point | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
43 | HN-7002 | Horn | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
44 | BR-7002 | Beacon - Red | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
45 | BB-7002 | Beacon - Blue | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
46 | BY-7002 | Beacon - Yellow | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
47 | MAC-8001 | Manual Call Point | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
48 | MAC-8002 | Manual Call Point | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
49 | HN-8001 | Horn | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
50 | BR-8001 | Beacon - Red | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
51 | BB-8001 | Beacon - Blue | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
52 | BY-8001 | Beacon - Yellow | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
53 | MAC-9001 | Manual Call Point | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
54 | MAC-9002 | Manual Call Point | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
55 | HN-9001 | Horn | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | 2X DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 5 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
56 | BR-9001 | Beacon - Red | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
57 | BB-9001 | Beacon - Blue | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
58 | BY-9001 | Beacon - Yellow | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Eexd Zone2, IIB T4 | DO-NIS-R |  | FGS |  | Field |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
59 | FGD-1001 | Flammable Gas Detector | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
60 | TGD-1001 | Toxic Gas Detector | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
61 | FD-2001 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
62 | FD-2002 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
63 | FD-2003 | Flame Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
64 | FGD-2001 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
65 | FGD-2002 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
66 | FGD-2003 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
67 | FGD-2004 | Flammable Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
68 | TGD-2001 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
69 | TGD-2002 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
70 | TGD-2003 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
71 | TGD-2004 | Toxic Gas Detector | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
72 | FD-3001 | Flame Detector | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (6 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
73 | FGD-3001 | Flammable Gas Detector | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (6 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
74 | TGD-3001 | Toxic Gas Detector | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (6 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
75 | FD-4001A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
76 | FD-4002A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
77 | FD-4003A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
78 | FD-4004A | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
79 | FGD-4001A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
80 | FGD-4002A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
81 | FGD-4003A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
82 | FGD-4004A | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
83 | TGD-4001A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
84 | TGD-4002A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
85 | TGD-4003A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
86 | TGD-4004A | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
87 | FD-4001B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
88 | FD-4002B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
89 | FD-4003B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
90 | FD-4004B | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
91 | FGD-4001B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
92 | FGD-4002B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
93 | FGD-4003B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
94 | FGD-4004B | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
95 | TGD-4001B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
96 | TGD-4002B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
97 | TGD-4003B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
98 | TGD-4004B | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
99 | FD-4001C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
100 | FD-4002C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
101 | FD-4003C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
102 | FD-4004C | Flame Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
103 | FGD-4001C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
104 | FGD-4002C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
105 | FGD-4003C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
106 | FGD-4004C | Flammable Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
107 | TGD-4001C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
108 | TGD-4002C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
109 | TGD-4003C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
110 | TGD-4004C | Toxic Gas Detector | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
111 | FGD-5001A | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
112 | FGD-5001B | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
113 | FGD-5001C | Flammable Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
114 | TGD-5001A | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
115 | TGD-5001B | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
116 | TGD-5001C | Toxic Gas Detector | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
117 | FD-6001 | Flame Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
118 | FD-6002 | Flame Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
119 | FGD-6001 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
120 | FGD-6002 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
121 | FGD-6003 | Flammable Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
122 | TGD-6001 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
123 | TGD-6002 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
124 | TGD-6003 | Toxic Gas Detector | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
125 | LHD-7001 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
126 | LHD-7002 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
127 | LHD-7003 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
128 | LHD-7004 | Linear Heat Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexd Zone2, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
129 | FGD-7001 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
130 | FGD-7002 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
131 | FGD-7003 | Flammable Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
132 | TGD-7001 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
133 | TGD-7002 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
134 | TGD-7003 | Toxic Gas Detector | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
135 | FD-8001 | Flame Detector | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (11 OF 12) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
FOR BUILDING
1 | FGD-1101 | Flammable Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * |  | √ | √ |  | Conventional |  | D02
2 | FGD-1102 | Flammable Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
3 | FGD-1103 | Flammable Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
4 | TGD-1101 | Toxic Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
5 | TGD-1102 | Toxic Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
6 | TGD-1103 | Toxic Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
7 | FGD-1201 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
8 | FGD-1202 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
9 | FGD-1203 | Flammable Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
10 | TGD-1201 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
11 | TGD-1202 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
12 | TGD-1203 | Toxic Gas Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Eexia Zone2, IIB T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 3 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
13 | HGD-1101 | Hydrogen Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
14 | HGD-1102 | Hydrogen Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
15 | HGD-1103 | Hydrogen Gas Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | AI-IS-R |  | Field |  | FGS |  | - | 4-20 mA | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * | √ | √ |  | Conventional |  | D02
16 | HD-1101 | Heat Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
17 | HD-1102 | Heat Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
18 | HD-1103 | Heat Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
18 | MAC-1102 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Eexd 'Zone1, IIC T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
SIGNALS BETWEEN F&G AND ESD SYSTEM & OTHER SYSTEMS
1 | ESD0-FG-1101 | ESD 0 Request | Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Unclassified | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
2 | ESD1A-FG-1101 | ESD 1A Request | Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Eexd 'Zone1, IIB T4 | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
3 | ESD2A-FG-1101A | ESD 2A(Train A) Request | Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Eexd 'Zone1, IIB T4 | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
4 | ESD2A-FG-1101B | ESD 2A(Train B) Request | Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Eexd 'Zone1, IIB T4 | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
5 | ESD2A-FG-1101C | ESD 2A(Train C) Request | Control Building |  | BK-GCS-PEDCO-120-IN-DG-0003 |  | Eexd 'Zone1, IIB T4 | DO-NIS-R |  | FGS |  | ESD |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
6 | FAN-FG-1101 | Battery Room Standby Fan Activation | Control Building |  | - |  | Eexd 'Zone1, IIB T4 | DO-NIS-R |  | FGS |  | IRP |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
7 | INB-FG-1101 | Inhibit to Boost for UPS Charger | Control Building |  | - |  | Eexd 'Zone1, IIB T4 | DO-NIS-R |  | FGS |  | UPS |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
8 | Ex-FG-G-1101 | F&G System confirmed Gas Alarm to Existing F&G | Control Building |  | - |  | Eexd 'Zone1, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
9 | Ex-FG-F-1101 | F&G System confirmed Fire Alarm to Existing F&G System | Control Building |  | - |  | Eexd 'Zone1, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
10 | Ex-FG-G-1102 | Existing F&G confirmed Gas Alarm to F&G System | Control Building |  | - |  | Eexd 'Zone1, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
11 | Ex-FG-F-1102 | Existing F&G confirmed Fire Alarm to F&G System | Control Building |  | - |  | Eexd 'Zone1, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
12 | LSLL-2301 | Low Low Level Alarm | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/1) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
13 | LSLL-2302 | Low Low Level Alarm | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/1) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R |  | Field |  | FGS |  | - | - | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
14 | HSS-2301A | Pump Start Command | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2301A | Battery Room Fan |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
15 | XL-2301A | Pump Local/ Remote Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
16 | XR-2301A | Pump Running/ Stopped Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
17 | XF-2301A | Pump Fault Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
18 | PAL-2301A | Low Pressure Alarm | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
19 | HSS-2301B | Pump Start Command | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2301B | Battery Room Fan |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
20 | XL-2301B | Pump Local/ Remote Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
21 | XR-2301B | Pump Running/ Stopped Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
22 | XF-2301B | Pump Fault Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
23 | PAL-2301B | Low Pressure Alarm | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2301B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
24 | HSS-2302A | Pump Start Command | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2302A | Battery Room Fan |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
25 | XL-2302A | Pump Local/ Remote Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
26 | XR-2302A | Pump Running/ Stopped Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
27 | XF-2302A | Pump Fault Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
28 | PAL-2302A | Low Pressure Alarm | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302A | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
29 | HSS-2302B | Pump Start Command | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DO-NIS-R | DO-NIS-R | FGS | FGS | P-2302B | Battery Room Fan |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
30 | XL-2302B | Pump Local/ Remote Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
31 | XR-2302B | Pump Running/ Stopped Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
32 | XF-2302B | Pump Fault Status | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
33 | PAL-2302B | Low Pressure Alarm | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0001(2/2) |  | Eexd 'Zone1, IIB T4 | DI-NIS-R | DI-NIS-R | P-2302B | Battery Room Fan | FGS | FGS |  | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | * |  |  |  | Conventional |  | D02
SIGNALS TO ESD/F&G MIMIC PANEL
1 | LAMP1-ACB-FD | Single Detection Fire Alarm Lamp for Control Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
2 | LAMP2-ACB-FD | Double Detection Fire Alarm Lamp for Control Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
3 | LAMP1-TGCA-FD | Single Detection Fire Alarm Lamp for Turbo Comp. A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
4 | LAMP2-TGCA-FD | Double Detection Fire Alarm Lamp for Turbo Comp. A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
5 | LAMP1-TGCB-FD | Single Detection Fire Alarm Lamp for Turbo Comp. B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
6 | LAMP2-TGCB-FD | Double Detection Fire Alarm Lamp for Turbo Comp. B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
7 | LAMP1-TGCC-FD | Single Detection Fire Alarm Lamp for Turbo Comp. C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
8 | LAMP2-TGCC-FD | Double Detection Fire Alarm Lamp for Turbo Comp. C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
9 | LAMP1-AC-FD | Single Detection Fire Alarm Lamp for Electrical Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
10 | LAMP2-AC-FD | Double Detection Fire Alarm Lamp for Electrical Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
11 | LAMP1-MVSG-FD | Single Detection Fire Alarm Lamp for Utility Area | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
12 | LAMP2-MVSG-FD | Double Detection Fire Alarm Lamp for Utility Area | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
13 | LAMP1-TCA-FGD | Unconfirmed Low FGD Alarm Lamp for Turbo Comp. A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
14 | LAMP2-TCA-FGD | Confirmed Low FGD Alarm Lamp for Turbo Comp. A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
15 | LAMP3-TCA-FGD | Unconfirmed High FGD Alarm Lamp for Turbo Comp. A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
16 | LAMP4-TCA-FGD | Confirmed High FGD Alarm Lamp for Turbo Comp. A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
17 | LAMP1-TCB-FGD | Unconfirmed Low FGD Alarm Lamp for Turbo Comp. B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
18 | LAMP2-TCB-FGD | Confirmed Low FGD Alarm Lamp for Turbo Comp. B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
19 | LAMP3-TCB-FGD | Unconfirmed High FGD Alarm Lamp for Turbo Comp. B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
20 | LAMP4-TCB-FGD | Confirmed High FGD Alarm Lamp for Turbo Comp. B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
21 | LAMP1-TCC-FGD | Unconfirmed Low FGD Alarm Lamp for Turbo Comp. C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
22 | LAMP2-TCC-FGD | Confirmed Low FGD Alarm Lamp for Turbo Comp. C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02(ADDED)
23 | LAMP3-TCC-FGD | Unconfirmed High FGD Alarm Lamp for Turbo Comp. C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
24 | LAMP4-TCC-FGD | Confirmed High FGD Alarm Lamp for Turbo Comp. C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
25 | LAMP1-GCA-FGD | Unconfirmed Low FGD Alarm Lamp for Gas Cooler A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
26 | LAMP2-GCA-FGD | Unconfirmed High FGD Alarm Lamp for Gas Cooler A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
27 | LAMP1-GCB-FGD | Unconfirmed Low FGD Alarm Lamp for Gas Cooler B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
28 | LAMP2-GCB-FGD | Unconfirmed High FGD Alarm Lamp for Gas Cooler B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
29 | LAMP1-GCC-FGD | Unconfirmed Low FGD Alarm Lamp for Gas Cooler C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
30 | LAMP2-GCC-FGD | Unconfirmed High FGD Alarm Lamp for Gas Cooler C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
31 | LAMP-SCA-FGD | FGD Alarm Lamp for Scrubber A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | [6 empty] | D02
32 | LAMP-SCB-FGD | FGD Alarm Lamp for Scrubber B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | [6 empty] | D02
33 | LAMP-SCC-FGD | FGD Alarm Lamp for Scrubber C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | [6 empty] | D02
34 | LAMP1-CR-FGD | Unconfirmed Low FGD Alarm Lamp for Control Building AIR Entrance | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
35 | LAMP2-CR-FGD | Confirmed Low FGD Alarm Lamp for Control Building AIR Entrance | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
36 | LAMP3-CR-FGD | Unconfirmed High FGD Alarm Lamp for Control Building AIR Entrance | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
37 | LAMP4-CR-FGD | Confirmed High FGD Alarm Lamp for Control Building AIR Entrance | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
38 | LAMP1-EB-FGD | Unconfirmed LowFGD Alarm Lamp for Electrical Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional
39 | LAMP2-EB-FGD | Confirmed Low FGD Alarm Lamp for Electrical Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
40 | LAMP3-EB-FGD | Unconfirmed High FGD Alarm Lamp for Electrical Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
41 | LAMP4-EB-FGD | Confirmed High FGD Alarm Lamp for Electrical Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
42 | LAMP-PA-FGD | FGD Alarm Lamp for Utility Area | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | [6 empty] | D02
43 | LAMP1-BR-HGD | Unconfirmed Low Hydrogen Gas Alarm Lamp for Battery Room | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
44 | LAMP2-BR-HGD | Confirmed Low Hydrogen Gas Alarm Lamp for Battery Room | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
45 | LAMP3-BR-HGD | Unconfirmed High Hydrogen Gas Alarm Lamp for Battery Room | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
46 | LAMP4-BR-HGD | Confirmed High Hydrogen Gas Alarm Lamp for Battery Room | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
47 | LAMP1-TCA-TGD | Unconfirmed Low TGD Alarm Lamp for Turbo Comp. A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
48 | LAMP2-TCA-TGD | Confirmed Low TGD Alarm Lamp for Turbo Comp. A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
49 | LAMP3-TCA-TGD | Unconfirmed High TGD Alarm Lamp for Turbo Comp. A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
50 | LAMP4-TCA-TGD | Confirmed High TGD Alarm Lamp for Turbo Comp. A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
51 | LAMP1-TCB-TGD | Unconfirmed Low TGD Alarm Lamp for Turbo Comp. B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
52 | LAMP2-TCB-TGD | Confirmed Low TGD Alarm Lamp for Turbo Comp. B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
53 | LAMP3-TCB-TGD | Unconfirmed High TGD Alarm Lamp for Turbo Comp. B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
54 | LAMP4-TCB-TGD | Confirmed High TGD Alarm Lamp for Turbo Comp. B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
55 | LAMP1-TCC-TGD | Unconfirmed Low TGD Alarm Lamp for Turbo Comp. C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
56 | LAMP2-TCC-TGD | Confirmed Low TGD Alarm Lamp for Turbo Comp. C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
57 | LAMP3-TCC-TGD | Unconfirmed High TGD Alarm Lamp for Turbo Comp. C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
58 | LAMP4-TCC-TGD | Confirmed High TGD Alarm Lamp for Turbo Comp. C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
59 | LAMP1-GCA-TGD | Unconfirmed Low TGD Alarm Lamp for Gas Cooler A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 10 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
60 | LAMP2-GCA-TGD | Unconfirmed High TGD Alarm Lamp for Gas Cooler A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 10 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
61 | LAMP1-GCB-TGD | Unconfirmed Low TGD Alarm Lamp for Gas Cooler B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
62 | LAMP2-GCB-TGD | Unconfirmed High TGD Alarm Lamp for Gas Cooler B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
63 | LAMP1-GCC-TGD | Unconfirmed Low TGD Alarm Lamp for Gas Cooler C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
64 | LAMP2-GCC-TGD | Unconfirmed High TGD Alarm Lamp for Gas Cooler C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
65 | LAMP-SCA-TGD | TGD Alarm Lamp for Scrubber A | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | [6 empty] | D02
66 | LAMP-SCAB-TGD | TGD Alarm Lamp for Scrubber B | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | [6 empty] | D02
67 | LAMP-SCC-TGD | TGD Alarm Lamp for Scrubber C | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | [6 empty] | D02
68 | LAMP1-CR-TGD | Unconfirmed Low TGD Alarm Lamp for Control Building AIR Entrance | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
69 | LAMP2-CR-TGD | Confirmed Low TGD Alarm Lamp for Control Building AIR Entrance | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
70 | LAMP3-CR-TGD | Unconfirmed High TGD Alarm Lamp for Control Building AIR Entrance | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
71 | LAMP4-CR-TGD | Confirmed High TGD Alarm Lamp for Control Building AIR Entrance | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
72 | LAMP1-EB-TGD | Unconfirmed Low TGD Alarm Lamp for Electrical Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
73 | LAMP2-EB-TGD | Confirmed Low TGD Alarm Lamp for Electrical Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
74 | LAMP3-EB-TGD | Unconfirmed Hig TGD Alarm Lamp for Electrical Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
75 | LAMP4-EB-TGD | Confirmed High TGD Alarm Lamp for Electrical Building | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
76 | LAMP-PA-TGD | TGD Alarm Lamp for Utility Area | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * | [6 empty] | D02
77 | LAMP-PA-FD | Fire Alarm Lamp for Utility Area | Control Building |  | BK-GCS-PEDCO-120-IN-DT-0017 |  | - | DO-NIS-R |  | FGS |  | F&G Matrix |  | - | 24 VDC | 2 Core x 1.5 | * | * | * | * | * | * | * | * |  |  |  |  | Conventional |  | D02
D02
D02
D02

## IO List for FACP
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR F&G SYSTEMS
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO | 120 |  | IN | LI | 0004 | D02
SIGNALS TO FACP
ITEM | TAG | DESCRIPTION | LOCATION |  | P&ID |  | SIGNAL TYPE/ Area CLASSIFICATION | I/O TYPE | FROM | TO |  | POWER SUPPLY | Cable Type | Marshalling Cabinet |  |  | ALARM |  |  |  | I/O TYPE (ADDRE./CONV.) | REMARK | REV.
[14 empty] | CABINET NO. | TB NO. | ADD. | HH | H | L | LL
FOR BUILDING
FACP LOOP 1
1 | FACP | Output Port of Loop 1 | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | MAC-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
2 | MAC-1104 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1104 | SD-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
3 | SD-1101 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1101 | SD-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
4 | SD-1102 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1102 | SD-1103 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
5 | SD-1103 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1103 | SD-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
6 | SD-1104 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1104 | SD-1105 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
7 | SD-1105 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1105 | SD-1106 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
8 | SD-1106 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1106 | SD-1107 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
9 | SD-1107 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1107 | SD-1108 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
10 | SD-1108 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1108 | MAC-1103 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
11 | MAC-1103 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1103 | HN-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
12 | HN-1102 | Horn | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | HN-1102 | BR-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
13 | BR-1102 | Beacon - Red | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BR-1102 | BB-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
14 | BB-1102 | Beacon - Blue | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BB-1102 | BY-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
15 | BY-1102 | Beacon - Yellow | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BY-1102 | MAC-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
16 | MAC-1101 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1101 | MAC-1106 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
17 | MAC-1106 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1106 | BR-1103 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
18 | BR-1103 | Beacon - Red | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BR-1103 | BL-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
19 | BL-1101 | Bell | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BL-1101 | SD-1109 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
20 | SD-1109 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1109 | BR-1104 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
21 | BR-1104 | Beacon - Red | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BR-1104 | MAC-1105 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
22 | MAC-1105 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1105 | BL-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
23 | BL-1102 | Bell | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BL-1102 | MAC-1109 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
24 | MAC-1109 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1109 | HN-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
25 | HN-1101 | Horn | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | HN-1101 | BR-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
26 | BR-1101 | Beacon - Red | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BR-1101 | BB-1101 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
27 | BB-1101 | Beacon - Blue | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BB-1101 | BY-1102 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
28 | BY-1102 | Beacon - Yellow | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BY-1102 | SD-1116 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
29 | SD-1116 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1116 | SD-1117 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
30 | SD-1117 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1117 | MAC-1107 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
31 | MAC-1107 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1107 | SD-1120 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
32 | SD-1120 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1120 | SD-1118 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
33 | SD-1118 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1118 | SD-1119 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
34 | SD-1119 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1119 | SD-1114 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
35 | SD-1114 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1114 | SD-1113 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
36 | SD-1113 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1113 | SD-1111 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
37 | SD-1111 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1111 | SD-1110 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
38 | SD-1110 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1110 | SD-1112 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
39 | SD-1112 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1112 | SD-1115 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
40 | SD-1115 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1115 | MAC-1108 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
41 | MAC-1108 | Manual Call Point | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | MAC-1108 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
42 | BL-1103 | Bell | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BL-1103 | SD-1114 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
43 | SD-1121 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1121 | SD-1122 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
44 | SD-1122 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1122 | SD-1123 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
45 | SD-1123 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1123 | SD-1124 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
46 | SD-1124 | Smoke Detector | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1124 | MAC-1105 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
47 | BL-1103 | Bell | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | BL-1103 | FACP |  | 24 VDC | Modbus Data | Note1 | [8 empty] | D02
FACP LOOP 2
1 | FACP | Output Port of Loop 2 | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | SD-1181 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
2 | SD-1181 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1181 | SD-1182 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
3 | SD-1182 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1182 | SD-1183 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
4 | SD-1183 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1183 | SD-1184 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
5 | SD-1184 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1184 | SD-1185 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
6 | SD-1185 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1185 | SD-1186 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
7 | SD-1186 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1186 | SD-1187 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
8 | SD-1187 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1187 | SD-1188 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
9 | SD-1188 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1188 | SD-1189 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
10 | SD-1189 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1189 | SD-1190 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
11 | SD-1190 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1190 | SD-1191 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
12 | SD-1191 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1191 | SD-1192 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
13 | SD-1192 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1192 | SD-1193 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
14 | SD-1193 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1193 | SD-1194 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
15 | SD-1194 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1194 | SD-1195 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
16 | SD-1195 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1195 | SD-1196 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
17 | SD-1196 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1196 | SD-1197 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
18 | SD-1197 | Smoke Detector | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1197 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
FACP LOOP 3
1 | FACP | Output Port of Loop 3 | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | SD-1150 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
2 | SD-1150 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1150 | SD-1151 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
3 | SD-1151 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1151 | SD-1152 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
4 | SD-1152 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1152 | SD-1153 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
5 | SD-1153 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1153 | SD-1154 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
6 | SD-1154 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1154 | SD-1155 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
7 | SD-1155 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1155 | SD-1156 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
8 | SD-1156 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1156 | SD-1157 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
9 | SD-1157 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1157 | SD-1158 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
10 | SD-1158 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1158 | SD-1159 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
11 | SD-1159 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1159 | SD-1160 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
12 | SD-1160 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1160 | SD-1161 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
13 | SD-1161 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1161 | SD-1162 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
14 | SD-1162 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1162 | SD-1163 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
15 | SD-1163 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1163 | SD-1164 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
16 | SD-1164 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1164 | SD-1165 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
17 | SD-1165 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1165 | SD-1166 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
18 | SD-1166 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1166 | SD-1167 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
19 | SD-1167 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1167 | SD-1168 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
20 | SD-1168 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1168 | SD-1169 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
21 | SD-1169 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1169 | SD-1170 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
22 | SD-1170 | Smoke Detector | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1170 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
FACP LOOP 4
1 | FACP | Output Port of Loop 4 | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | HN-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
2 | HN-1201 | Horn | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | HN-1201 | BR-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
3 | BR-1201 | Beacon - Red | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BR-1201 | BB-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
4 | BB-1201 | Beacon - Blue | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BB-1201 | MAC-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
5 | BY-1201 | Beacon - Yellow | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BY-1201 | SD-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
6 | MAC-1201 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1201 | SD-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
7 | SD-1201 | Smoke Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | SD-1201 | SD-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
8 | SD-1202 | Smoke Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | SD-1202 | MAC-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
9 | MAC-1202 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1202 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
FACP LOOP 5
1 | FACP | Output Port of Loop 5 | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | HN-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
2 | HN-1202 | Horn | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | HN-1202 | BR-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
3 | BR-1202 | Beacon - Red | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | BR-1202 | BY-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
4 | BB-1202 | Beacon - Blue | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | BB-1202 | BY-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
5 | BY-1202 | Beacon - Yellow | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | BY-1202 | MAC-1203 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
6 | MAC-1203 | Manual Call Point | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | MAC-1203 | LHD-1201 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
7 | LHD-1201 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | LHD-1201 | LHD-1202 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
8 | LHD-1202 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | LHD-1202 | LHD-1203 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
9 | LHD-1203 | Linear Heat Detector | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Note 1 | Note1 | LHD-1203 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
FACP LOOP 6
1 | FACP | Output Port of Loop 6 | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | FACP | SD-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
2 | SD-1301 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1301 | SD-1302 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
3 | SD-1302 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1302 | SD-1303 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
4 | SD-1303 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1303 | MAC-1303 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
5 | MAC-1303 | Manual Call Point | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1303 | SD-1304 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
6 | SD-1304 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1304 | SD-1305 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
7 | SD-1305 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1305 | SD-1306 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
8 | SD-1306 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1306 | SD-1307 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
9 | SD-1307 | Smoke Detector | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Note 1 | Note1 | SD-1307 | MAC-1302 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
10 | MAC-1302 | Manual Call Point | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1302 | MAC-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
11 | MAC-1301 | Manual Call Point | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | MAC-1301 | HN-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
12 | HN-1301 | Horn | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | HN-1301 | BR-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
13 | BR-1301 | Beacon - Red | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BR-1301 | BB-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
14 | BB-1301 | Beacon - Blue | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BB-1301 | BY-1301 |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
15 | BY-1301 | Beacon - Yellow | Telecom Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Note 1 | Note1 | BY-1301 | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
SIGNALS BETWEEN FACP AND CO2 CONTROL PACKAGE
1 | XA-CO2-1101 | MANUAL/AUTO SELECTOR SWITCH STATUS (FOR PROTECTED AREA) | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R | CO2 Control Panel | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
2 | XRE-CO2-1101 | RELEASED STATUS (FOR PROTECTED AREA) | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R | CO2 Control Panel | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
3 | XI-CO2-1101 | INHIBIT STATUS (FOR PROTECTED AREA) | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R | CO2 Control Panel | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
4 | XF-CO2-1101 | GENERAL FAULT | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DI-NIS-R | CO2 Control Panel | FACP |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
5 | HS-CO2-1101 | AUTOMAT RELEASE COMMAND (FOR PROTECTED AREA) | Control Building |  | BK-GCS-PEDCO-120-SA-PI-0002 |  | - | DO-NIS-R | FACP | CO2 Control Panel |  | 24 VDC | Modbus Data | Note1 | [6 empty] | ADDRESSABLE |  | D02
Notes:
1- Non-IS Detector is on the Loop. Level of Alarm is N.A. for such Loop-powered.
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02