## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
Data Sheets For Pressure & Diff. Pressure Gauge
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 7
9184 – 073 - 053 |  |  | BK |  | PPL | PEDCO | 320 |  | IN | DT | 0001 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR PRESSURE & DIFF. PRESSURE GAUGE نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | SEP.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | APR.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | JAN.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F9Z708581
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
Data Sheets For Pressure & Diff. Pressure Gauge
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 7
9184 – 073 - 053 |  |  | BK | PPL |  | PEDCO | 320 | IN | DT | 0001 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | X | [5 empty] | 67
4 | X | X | X | [5 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 |  |  | X | [5 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Table of Content
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
Data Sheets For Pressure & Diff. Pressure Gauge
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 3 از 7
9184 – 073 - 053 |  | BK | PPL | PEDCO | 320 | IN | DT | 0001 | D02
TABLE OF CONTENT
| CONTENT | [8 empty] | SHEET NUMBER
| COVER | [8 empty] | 1
| REVISION SHEET | [8 empty] | 2
| TABLE OF CONTENT | [8 empty] | 3
| REFERENCES | [8 empty] | 4
| NOTES | [8 empty] | 5
| PRESSURE GAUGE REQUIREMENTS | [8 empty] | 6
| PRESSURE GAUGES LIST | [8 empty] | 7
D02

## Reference
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
Data Sheets For Pressure & Diff. Pressure Gauge
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 7
9184 – 073 - 053 |  |  | BK | PPL | PEDCO | 320 | IN |  | DT | 0001 | D02
REFERENCE DOCUMENTS :
|  | Instrument & Control System Design Criteria | [5 empty] | BK-PPL-PEDCO-320-IN-DC-0001_D01
|  | P&ID - Gas Pipeline (to Siahmakan G.I. Station) | [5 empty] | BK-PPL-PEDCO-320-PR-PI-0001_D03
|  | P&ID - Condensate Pipeline (to Binak PU) | [5 empty] | BK-PPL-PEDCO-320-PR-PI-0002_D03
|  | Piping Material Specification | [5 empty] | BK-GCS-PEDCO-120-PI-SP-0001_D01
|  | Specification For Instrumentation | [5 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001_D04
|  | Instrument Hook-Up Diagram | [5 empty] | BK-PPL-PEDCO-320-IN-DG-0002_D00
D02

## Notes
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
Data Sheets For Pressure & Diff. Pressure Gauge
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 7
9184 – 073 - 053 |  |  |  | BK | PPL | PEDCO | 320 | IN | DT | 0001 | D02
GENERAL NOTES:
1- Ranges shall be selected suitable to have the operating pressure in the middle third of the scale.
2- Vendor is responsible for applying suitable accessories to prevent damage and to reach required accuracy for PG.
3- Vendor to follow materials indicated in the Data Sheets, related wetted parts, these materials can be as minimum and shall be verified by vendor.
4- Gauges shall be supplied with syphon on steam services which operating temperatures are more than 100⁰c.
5- Tag plate shall be stainless steel. Following details shall be engraved on them:
- Tag Number
- Range limit
- Service
- Manufacturer model and serial number
6- Weep hole shall be provided on the case bottom of all gauges.
7- Material Test Certificate and Calibration Certificate for all gauges to be submitted by vendor.
8- Each pressure gauge which doesn’t have Diaphragm Seal shall be supplied with a Two-Way manifold (Process Conn. 1/2"NPTF, 316 S.S.). Manifold to be supplied by vendor.
9-According to "Process Basic of Design" Document, Environmental Condition For Field Instrumentation of BINAK Complex Shall Be Considered As Per The Following:
Maximum ambient temperature: 50 (°C)
Minimum ambient temperature: 5 (°C)
Maximum steel surface exposed to sun: 85 (°C)
Maximum summer dry bulb: 50 (°C)
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0
D02

## PG
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
Data Sheets For Pressure & Diff. Pressure Gauge
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 6 از 7
9184 – 073 - 053 |  |  |  | BK | PPL | PEDCO | 320 | IN | DT | 0001 | D02
PRESSURE GAUGE
| GENERAL | 1 | Tag No. |  | P&ID No. |  |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  | 2 | Service |  | Piping Class |  |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  | 3 | Area Clacification |  |  |  |  | Zone 2, IIB T4
| PROCESS CONDITION | 4 | Fluid |  | Phase |  |  | SEE PAGE 6 |  |  | SEE PAGE 6
|  | 5 | Operating. Pressure |  | Design. Pressure |  |  | SEE PAGE 6 |  |  | SEE PAGE 6 |  |  |  |  | (barg)
|  | 6 | Operating. Temperature |  | Design. Temperature |  |  | SEE PAGE 6 |  |  | SEE PAGE 6 |  |  |  |  | (°C)
|  | 7 | Min. Design Metal Temperature |  |  |  |  | SEE PAGE 6 | [7 empty] | (°C)
|  | 8 | Range |  |  |  |  | SEE PAGE 6
| GAUGE | 9 | Type |  |  |  |  | Pressure Gauge-Direct Reading
|  | 10 | Instrument Range |  |  |  |  | SEE PAGE 6
|  | 11 | Liquid Filled |  |  |  |  | Silicon - SEE PAGE 6 |  |  |  | (Note 5)
|  | 12 | Mounting |  |  |  |  | Local
|  | 13 | Dial Size |  | Dial Color | Zero Adjustment |  | 150 mm |  |  | White with black lettering |  |  |  | Adjustable pointer
|  | 14 | Case Material |  |  |  |  | 304 SS |  |  |  | (Note 2)
|  | 15 | Blow-Out Protection |  |  |  |  | Solid front
|  | 16 | Lens Material |  |  |  |  | Shatter proof glass
|  | 17 | Pressure Element Type |  |  |  |  | SEE PAGE 6
|  | 18 | Pressure Element Material |  |  |  |  | SEE PAGE 6
|  | 19 | Connection Material |  |  |  |  | 316 S.S
|  | 20 | Connection Size |  |  |  |  | 1/2 " NPT
|  | 21 | Connection Location |  |  |  |  | Bottom
|  | 22 | Movement Material |  |  |  |  | 316 S.S
|  | 23 | Nominal Accuracy |  |  |  |  | 0.6% F.S
|  | 24 | Weather Protection |  |  |  |  | IP-65 as minimum
| DIAPHRAGM SEAL | 25 | Type |  |  |  |  | N/A
|  | 26 | Size (In) |  |  |  |  | N/A
|  | 27 | Diaphragm Material |  |  |  |  | N/A
|  | 28 | Fill Fluid |  |  |  |  | N/A
|  | 29 | Capillary Length |  |  |  |  | N/A
|  | 30 | Capillary Material |  |  |  |  | N/A
31
| OPTIONS | 32 | Movement Damping |  |  |  |  | SEE PAGE 6
|  | 33 | Overrange Protection |  |  |  |  | SEE PAGE 6 (1.3 of F.S) (Note 7)
|  | 34 | Siphon |  | Material |  |  | SEE PAGE 6 | [6 empty] | 316L S.S
|  | 35 | Manifold |  | Body Material |  |  | 2 Way Manifold | [6 empty] | 316L S.S
|  | 36 | Process Connection |  | Rating |  |  | SEE PAGE 6 (Note 6) | [6 empty] | SEE PAGE 6
|  | 37 | Manifold Model |  | Manifold Manufacturer |  |  | VTA | [6 empty] | VTA
|  | 38 | NACE Requirements |  |  |  |  | SEE PAGE 6 | [5 empty] | (Note 1)
39
40
| PURCHASING DATA | 41 | Model No. |  | Manufacturer |  |  | Will Be Finalized Later |  |  |  |  | Will Be Finalized Later
|  | 42 | Supplier |  | Order |  |  | Will Be Finalized Later |  |  |  |  | Will Be Finalized Later
43
44
| NOTES : | VTA : Vendor to Advise
(1) Requirements of BK-GNRAL-PEDCO-000-PI-SP-0008 and NACE-MR-0175/ISO 15156 shall be covered where in Piping/Pipeline Material Specification recommended.
(2) Window shall be heavy plate glass, breakage resistance and shatter proof.
(3) Pressure gauges shall be double scale type (Bar and Psi).
(4) All gauges shall be equipped with screw driver slot type adjustment for calibration purposes.
(5) All gauges near pumps and compressors that have vibration shall be equipped with adjustable restriction snubber.
(6) 1/2"NPT for Instrument/Process connection and 1/4" NPT for Drain Connection-All Manifolds, Pulsation Dampeners and Siphons shall be suitable for connecting to gauges.
(7) Over range protection shall be 1.3 times the maximum range.
D02

## PG LIST
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
Data Sheets For Pressure & Diff. Pressure Gauge
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 7 از 7
9184 – 073 - 053 |  |  |  |  | BK | PPL | PEDCO |  | 320 | IN |  | DT |  | 0001 |  | D02
PRESSURE GAUGE
Rev. | Item No. | Tag No. | P&IDs No. | Service. | LINE/ EQUIPMENT | Piping Class | Process Connection | Fluid | Phase | Operating Pressure (barg) | Design Pressure (barg) | Operating Temperature (°C) | Design Temperature(°C) | Range (barg) | Liquid. Filled | Press. Element Type | Press. Element Material | Movement Damping | Over Range Protection | Snubber | Siphon | Diaphragm Seal | Nace | Model | Remark
| 1 | PG-3201 | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) | On Pig Launcher | PL-3201 | -- | 1/2" NPT | GAS | GAS | 50.9 | 62 | 58.3 | 85 | 0-100 | Yes | Bourdon | SS 316L | NO | NO | NO | No | No | Yes | VTA | Note Page
| 2 | PG-3202 | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) | After Pig Launcher | GAS-113-0005-FN05-8"-PT | FN05 | 1/2" NPT | GAS | GAS | 50.9 | 62 | 58.3 | 85 | 0-100 | Yes | Bourdon | SS 316L | NO | NO | NO | No | No | Yes | VTA | Note Page
| 3 | PG-3203 | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) | Before Pig Receiver | GAS-113-0011-FN05-8"-PT | FN05 | 1/2" NPT | GAS | GAS | 40 | 62 | 31.3 | 85 | 0-60 | Yes | Bourdon | SS 316L | NO | NO | NO | No | No | Yes | VTA | Note Page
| 4 | PG-3204 | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) | Before Pig Receiver | GAS-113-0011-FN05-8"-PT | FN05 | 1/2" NPT | GAS | GAS | 40 | 62 | 31.3 | 85 | 0-60 | Yes | Bourdon | SS 316L | NO | NO | NO | No | No | Yes | VTA | Note Page
| 5 | PG-3205 | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) | On Pig Receiver | PR-3201 | -- | 1/2" NPT | GAS | GAS | 40 | 62 | 31.3 | 85 | 0-60 | Yes | Bourdon | SS 316L | NO | NO | NO | No | No | Yes | VTA | Note Page
D02 DELETED | 6 | PG-3210 | BK-PPL-PEDCO-320-PR-PI-0002 | On Piping to Binak Production Unit | CDH-112-0016-CN05-4"-PT | CN05 | 1/2" NPT | OIL (CONDENSATE) | 1PHASE (LIQUID) | 12.78 | 62 | 49.9 | 85 | 0-100 | Yes | Bourdon | SS 316L | NO | Yes | NO | No | No | Yes | VTA | Note Page
D02