## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-IN-DT-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0883 |  |  | Transmital Date: 30 APR 2022
Document Title: Data Sheets For Pressure & Diff. Pressure Gauge |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0105-IN-TR-0883 |  |  | Transmital Date: 30 APR 2022
[5 empty] | CRS No: NISOC-CRS-BK-PPL-PEDCO-320-IN-DT-0001_D01 |  |  | CRS Status: | C2
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در خصوص مورد 1 و 2 نظر خاصی مطرح نمی باشد. |  | 1401-2294-70739 | 1401/02/31 | -
2 | در خصوص مورد 3 نظر این امور اعمال نشده است. اعمال گردد. (Accuracy فشار سنج بهتر از 0.6 درصد F.S. در نظر گرفته شود. |  | 1401-2294-70739 | 1401/02/31 | اصلاح شد.
3 | در خصوص مورد 4 نظر این امور اعمال نشده است. اعمال گردد. (با توجه به نبود اندازه گیر اختلاف فشار در مدرک، عبارت اختلاف فشار از عنوان مدرک حذف و تصحیحات لازم در مدارک مربوطه از جمله MDL صورت پذیرد. |  | 1401-2294-70739 | 1401/02/31 | اصلاح شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: 13 Feb 2022 |  |  |  |  | Date: