## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
F&G DETECTOR LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 14
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0008 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
F&G DETECTOR LIST نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | OCT.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAY.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number:F0Z-708974
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
F&G DETECTOR LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 14
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0008 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | X | [5 empty] | 67
4 | X | X | X | [5 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | X | [5 empty] | 71
8 | X | X | X | [5 empty] | 72
9 | X | X | X | [5 empty] | 73
10 |  | X | X | [5 empty] | 74
11 |  | X | X | [5 empty] | 75
12 |  | X | X | [5 empty] | 76
13 |  | X | X | [5 empty] | 77
14 |  |  | X | [5 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REF & NOTE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
F&G DETECTOR LIST
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 14
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0008 | D02
REFERENCES(Note1):
| F&G LOCATION LAYOUT FOR PROCESS AREA | [7 empty] | BK-GCS-PEDCO-120-IN-PY-0005
| F&G LOCATION LAYOUT FOR BUILDINGS | [7 empty] | BK-GCS-PEDCO-120-IN-PY-0006
GENERAL NOTE
| 1 | Refer to latest version of reference documents.
| 2 | Sensor type of detectors is determined in document "DATA SHEETS FOR F&G DETECTORS & EQUIPMENT, BK-GCS-PEDCO-120-IN-DT-0016 "

## ABBREVIATION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
F&G DETECTOR LIST
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 14
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0008 | D02
ABBREVIATION:
| MAC | MANUAL CALL POINT
| HN | HORN
| BB | BLUE BEACON
| BR | RED BEACON
| LHD | LINEAER HEAT DETECTOR
| SD | SMOKE DETECTOR
| BL | BELL
| FGD | FLAMMABLE GAS DETECTOR
| TGD | TOXIC GAS DETECTOR
| FD | FLAME DETECTOR

## INDEX
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI |  | 0008 |  | D02
F&G DETECTOR LIST
ITEM | TAG | DESCRIPTION |  |  | LOCATION |  | F&G DETECTION LAYOUT DRAWING |  | AREA CLASSIFICATION | I/O TYPE |  | DATA SHEET |  | I/O TYPE (ADDRE./CONV.) | REMARK | REV.
FOR PROCESS AREA
1 | MAC-1001 | Manual Call Point |  |  | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
2 | MAC-1002 | Manual Call Point |  |  | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
3 | HN-1001 | Horn |  |  | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
4 | BR-1001 | Beacon - Red |  |  | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
5 | BB-1001 | Beacon - Blue |  |  | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
6 | BY-1001 | Beacon - Yellow |  |  | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
7 | MAC-2001 | Manual Call Point |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
8 | MAC-2002 | Manual Call Point |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
9 | MAC-2003 | Manual Call Point |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
10 | HN-2001 | Horn |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
11 | BR-2001 | Beacon - Red |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
12 | BB-2001 | Beacon - Blue |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
13 | BY-2001 | Beacon - Yellow |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
14 | MAC-3001 | Manual Call Point |  |  | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
15 | HN-3001 | Horn |  |  | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
16 | BR-3001 | Beacon - Red |  |  | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
17 | BB-3001 | Beacon - Blue |  |  | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
18 | BY-3001 | Beacon - Yellow |  |  | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
19 | MAC-4001 | Manual Call Point |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
20 | MAC-4002 | Manual Call Point |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
21 | HN-4001 | Horn |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
22 | BR-4001 | Beacon - Red |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
23 | BB-4001 | Beacon - Blue |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
24 | BY-4001 | Beacon - Yellow |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
25 | HN-4002 | Horn |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
26 | BR-4002 | Beacon - Red |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
27 | BB-4002 | Beacon - Blue |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
28 | BY-4002 | Beacon - Yellow |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
29 | MAC-5001 | Manual Call Point |  |  | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
30 | MAC-5002 | Manual Call Point |  |  | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
31 | HN-5001 | Horn |  |  | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
32 | BR-5001 | Beacon - Red |  |  | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
33 | BB-5001 | Beacon - Blue |  |  | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
34 | BY-5001 | Beacon - Yellow |  |  | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
35 | MAC-6001 | Manual Call Point |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
36 | MAC-6002 | Manual Call Point |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
37 | HN-6001 | Horn |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
38 | BR-6001 | Beacon - Red |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
39 | BB-6001 | Beacon - Blue |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
40 | BY-6001 | Beacon - Yellow |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
41 | MAC-7001 | Manual Call Point |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
42 | MAC-7002 | Manual Call Point |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
43 | HN-7002 | Horn |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
44 | BR-7002 | Beacon - Red |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
45 | BB-7002 | Beacon - Blue |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
46 | BY-7002 | Beacon - Yellow |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
47 | MAC-8001 | Manual Call Point |  |  | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
48 | MAC-8002 | Manual Call Point |  |  | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
49 | HN-8001 | Horn |  |  | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
50 | BR-8001 | Beacon - Red |  |  | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
51 | BB-8001 | Beacon - Blue |  |  | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
52 | BY-8001 | Beacon - Yellow |  |  | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
53 | MAC-9001 | Manual Call Point |  |  | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
54 | MAC-9002 | Manual Call Point |  |  | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
55 | HN-9001 | Horn |  |  | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
56 | BR-9001 | Beacon - Red |  |  | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
57 | BB-9001 | Beacon - Blue |  |  | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
58 | BY-9001 | Beacon - Yellow |  |  | Area 9 - Air Compressor /Air Dryer Packages Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (3 of 12) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
59 | FGD-1001 | Flammable Gas Detector |  |  | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
60 | TGD-1001 | Toxic Gas Detector |  |  | Area 1 - Pig Receiver Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (4 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
61 | FD-2001 | Flame Detector |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
62 | FD-2002 | Flame Detector |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
63 | FD-2003 | Flame Detector |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
64 | FGD-2001 | Flammable Gas Detector |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
65 | FGD-2002 | Flammable Gas Detector |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
66 | FGD-2003 | Flammable Gas Detector |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
67 | FGD-2004 | Flammable Gas Detector |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
68 | TGD-2001 | Toxic Gas Detector |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
69 | TGD-2002 | Toxic Gas Detector |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
70 | TGD-2003 | Toxic Gas Detector |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
71 | TGD-2004 | Toxic Gas Detector |  |  | Area 2 - Slug Catcher System Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (5 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
72 | FD-3001 | Flame Detector |  |  | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (6 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
73 | FGD-3001 | Flammable Gas Detector |  |  | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (6 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
74 | TGD-3001 | Toxic Gas Detector |  |  | Area 3 - Chemical Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (6 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
75 | FD-4001A | Flame Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
76 | FD-4002A | Flame Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
77 | FD-4003A | Flame Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
78 | FD-4004A | Flame Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
79 | FGD-4001A | Flammable Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
80 | FGD-4002A | Flammable Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
81 | FGD-4003A | Flammable Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
82 | FGD-4004A | Flammable Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
83 | TGD-4001A | Toxic Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
84 | TGD-4002A | Toxic Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
85 | TGD-4003A | Toxic Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
86 | TGD-4004A | Toxic Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
87 | FD-4001B | Flame Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
88 | FD-4002B | Flame Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
89 | FD-4003B | Flame Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
90 | FD-4004B | Flame Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
91 | FGD-4001B | Flammable Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
92 | FGD-4002B | Flammable Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
93 | FGD-4003B | Flammable Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
94 | FGD-4004B | Flammable Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
95 | TGD-4001B | Toxic Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
96 | TGD-4002B | Toxic Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
97 | TGD-4003B | Toxic Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
98 | TGD-4004B | Toxic Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
99 | FD-4001C | Flame Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
100 | FD-4002C | Flame Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
101 | FD-4003C | Flame Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
102 | FD-4004C | Flame Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
103 | FGD-4001C | Flammable Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
104 | FGD-4002C | Flammable Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
105 | FGD-4003C | Flammable Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
106 | FGD-4004C | Flammable Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
107 | TGD-4001C | Toxic Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
108 | TGD-4002C | Toxic Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
109 | TGD-4003C | Toxic Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
110 | TGD-4004C | Toxic Gas Detector |  |  | Area 4 - 1St. & 2nd Stage Gas Compressor Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (7 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
111 | FGD-5001A | Flammable Gas Detector |  |  | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
112 | FGD-5001B | Flammable Gas Detector |  |  | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
113 | FGD-5001C | Flammable Gas Detector |  |  | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
114 | TGD-5001A | Toxic Gas Detector |  |  | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
115 | TGD-5001B | Toxic Gas Detector |  |  | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
116 | TGD-5001C | Toxic Gas Detector |  |  | Area 5 - 1St. & 2nd Stage Air Cooler Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (8 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
117 | FD-6001 | Flame Detector |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
118 | FD-6002 | Flame Detector |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
119 | FGD-6001 | Flammable Gas Detector |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
120 | FGD-6002 | Flammable Gas Detector |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
121 | FGD-6003 | Flammable Gas Detector |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
122 | TGD-6001 | Toxic Gas Detector |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
123 | TGD-6002 | Toxic Gas Detector |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
124 | TGD-6003 | Toxic Gas Detector |  |  | Area 6 - Sump & Pig Launcher Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (9 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
125 | LHD-7001 | Linear Heat Detector |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
126 | LHD-7002 | Linear Heat Detector |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
127 | LHD-7003 | Linear Heat Detector |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
128 | LHD-7004 | Linear Heat Detector |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
129 | FGD-7001 | Flammable Gas Detector |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
130 | FGD-7002 | Flammable Gas Detector |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
131 | FGD-7003 | Flammable Gas Detector |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
132 | TGD-7001 | Toxic Gas Detector |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
133 | TGD-7002 | Toxic Gas Detector |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
134 | TGD-7003 | Toxic Gas Detector |  |  | Area 7 - Lean Glycol Storage Tank &Dehydration Package Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (10 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
135 | FD-8001 | Flame Detector |  |  | Area 8 - Diesel Generator Area |  | BK-GCS-PEDCO-120-IN-PY-0005 (11 of 12) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
FOR BUILDINGS
1 | HN-1101 | Horn |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
2 | BR-1101 | Beacon - Red |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
3 | BB-1101 | Beacon - Blue |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
4 | BY-1101 | Beacon - Yellow |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
5 | HN-1102 | Horn |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
6 | BR-1102 | Beacon - Red |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
7 | BB-1102 | Beacon - Blue |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
8 | BY-1102 | Beacon - Yellow |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
9 | BR-1103 | Beacon - Red |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
10 | BR-1104 | Beacon - Red |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
11 | HGD-1101 | Hydrogen Gas Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone1, IIC T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
12 | HGD-1102 | Hydrogen Gas Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone1, IIC T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
13 | HGD-1103 | Hydrogen Gas Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone1, IIC T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
14 | MAC-1101 | Manual Call Point |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
15 | MAC-1102 | Manual Call Point |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone1, IIC T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
16 | MAC-1103 | Manual Call Point |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
17 | MAC-1104 | Manual Call Point |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
18 | MAC-1105 | Manual Call Point |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
19 | MAC-1106 | Manual Call Point |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
20 | MAC-1107 | Manual Call Point |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
21 | MAC-1108 | Manual Call Point |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
22 | MAC-1109 | Manual Call Point |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
23 | FGD-1101 | Flammable Gas Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
24 | FGD-1102 | Flammable Gas Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
25 | FGD-1103 | Flammable Gas Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
26 | TGD-1101 | Toxic Gas Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
27 | TGD-1102 | Toxic Gas Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
28 | TGD-1103 | Toxic Gas Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
29 | SD-1101 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
30 | SD-1102 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
31 | SD-1103 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
32 | SD-1104 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
33 | SD-1105 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
34 | SD-1106 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
35 | SD-1107 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
36 | SD-1108 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
37 | SD-1109 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
38 | SD-1110 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone1, IIC T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
39 | SD-1111 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone1, IIC T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
40 | SD-1112 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone1, IIC T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
41 | SD-1113 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone1, IIC T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
42 | SD-1114 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
43 | SD-1115 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
44 | SD-1116 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
45 | SD-1117 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
46 | SD-1118 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
47 | SD-1119 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
48 | SD-1120 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
49 | SD-1121 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/5) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  |  |  | D02
50 | SD-1122 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/5) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  |  |  | D02
51 | SD-1123 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/5) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  |  |  | D02
52 | SD-1124 | Smoke Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/5) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  |  |  | D02
53 | SD-1181 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
54 | SD-1182 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
55 | SD-1183 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
56 | SD-1184 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
57 | SD-1185 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
58 | SD-1186 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
59 | SD-1187 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
60 | SD-1188 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
61 | SD-1189 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
62 | SD-1190 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
63 | SD-1191 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
64 | SD-1192 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
65 | SD-1193 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
66 | SD-1194 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
67 | SD-1195 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
68 | SD-1196 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
69 | SD-1197 | Smoke Detector |  |  | Control Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
70 | SD-1150 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
71 | SD-1151 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
72 | SD-1152 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
73 | SD-1153 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
74 | SD-1154 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
75 | SD-1155 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
76 | SD-1156 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
77 | SD-1157 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
78 | SD-1158 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
79 | SD-1159 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
80 | SD-1160 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
81 | SD-1161 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
82 | SD-1162 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
83 | SD-1163 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
84 | SD-1164 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
85 | SD-1165 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
86 | SD-1166 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
87 | SD-1167 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
88 | SD-1168 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
89 | SD-1169 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
90 | SD-1170 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
91 | SD-1171 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
92 | SD-1172 | Smoke Detector |  |  | Control Building-False Ceiling |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
93 | HD-1101 | Heat Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone1, IIC T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
94 | HD-1102 | Heat Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone1, IIC T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
95 | HD-1103 | Heat Detector |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Zone1, IIC T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
96 | BL-1101 | Bell |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
97 | BL-1102 | Bell |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/6) |  | Unclassified | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
98 | BL-1103 | Bell |  |  | Control Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (2/5) |  | Unclassified | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  |  |  | D02
99 | FGD-1201 | Flammable Gas Detector |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
100 | FGD-1202 | Flammable Gas Detector |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
101 | FGD-1203 | Flammable Gas Detector |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
102 | TGD-1201 | Toxic Gas Detector |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
103 | TGD-1202 | Toxic Gas Detector |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
104 | TGD-1203 | Toxic Gas Detector |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (3/6) |  | Zone2, IIB T4 | AI-IS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Conventional |  | D02
105 | SD-1201 | Smoke Detector |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
106 | SD-1202 | Smoke Detector |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
107 | SD-1211 | Smoke Detector |  |  | Extension of Existing Elect. Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
108 | SD-1212 | Smoke Detector |  |  | Extension of Existing Elect. Building-False Floor |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
109 | HN-1201 | Horn |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
110 | BR-1201 | Beacon - Red |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
111 | BB-1201 | Beacon - Blue |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
112 | BY-1201 | Beacon - Yellow |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
113 | MAC-1201 | Manual Call Point |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
114 | MAC-1202 | Manual Call Point |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
115 | HN-1202 | Horn |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
116 | BR-1202 | Beacon - Red |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
117 | BB-1202 | Beacon - Blue |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
118 | BY-1202 | Beacon - Yellow |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
119 | MAC-1203 | Manual Call Point |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
120 | LHD-1201 | Linear Heat Detector |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
121 | LHD-1202 | Linear Heat Detector |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
122 | LHD-1203 | Linear Heat Detector |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (5/6) |  | Zone2, IIB T4 | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
123 | HN-1301 | Horn |  |  | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
124 | BR-1301 | Beacon - Red |  |  | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
125 | BB-1301 | Beacon - Blue |  |  | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
126 | BY-1301 | Beacon - Yellow |  |  | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/6) |  | Zone2, IIB T4 | DO-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
127 | SD-1301 | Smoke Detector |  |  | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
128 | SD-1302 | Smoke Detector |  |  | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
129 | SD-1303 | Smoke Detector |  |  | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
130 | SD-1304 | Smoke Detector |  |  | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
131 | SD-1305 | Smoke Detector |  |  | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
132 | SD-1306 | Smoke Detector |  |  | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
133 | SD-1307 | Smoke Detector |  |  | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
134 | MAC-1301 | Manual Call Point |  |  | CCTV Control Room |  | BK-GCS-PEDCO-120-IN-PY-0006 (6/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
135 | MAC-1302 | Manual Call Point |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
136 | MAC-1303 | Manual Call Point |  |  | Extension of Existing Elect. Building |  | BK-GCS-PEDCO-120-IN-PY-0006 (4/6) |  | Unclassified | DI-NIS-R |  | BK-GCS-PEDCO-120-IN-DT-0016 |  | Addressable |  | D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02