## Index (hidden)
Attachment #1: Cable sizing calculation Tables for MV and LV Cables
Item no. | Sheet | Circuit | Voltage | AG/UG | 3C/1C
1
2
3
4
5
6
7 | [5 empty] | `
8
9
10
11
12
13
14
15
16
17

## MV Feeder- 11kV-3C-AG
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 11kV 3C AG
|  |  |  | System Nominal Voltage |  |  | 11 | (kV) |  | Standard |  |  | IEC |  | Derating factor |  |  | 0.61
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 10 / 11 kV |  | Installation
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  | Base Temperature (A/G) |  |  | 50
[10 empty] | Number of Cores |  |  | 3C |  | Base Temperature (U/G) |  |  | 35
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1
[5 empty] | Size | 50 | 70 | 95 | 120 | 150 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 205 | 253 | 307 | 352 | 397 | 453 | 529 | [7 empty] | Page 54 of MV Cable Abhar
Resistance (ohm/km) | [5 empty] | 0.494 | 0.342 | 0.247 | 0.196 | 0.159 | 0.1277 | 0.098 | [7 empty] | Page 26 of MV Cable Abhar
Reactance (ohm/km) | [5 empty] | 0.13 | 0.123 | 0.117 | 0.111 | 0.108 | 0.104 | 0.1
Derated Ampacity (A) | [5 empty] | 125.05 | 154.33 | 187.27 | 214.72 | 242.17 | 276.33 | 322.69 |  | 0 | 0 | 0 | 0 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
- | 1250 | 65.608 | 80 | 100 | 95 |  |  | 3614.6378 | 4333.0349 | 5041.6667 | 5882.3529 | 6994.2197

## MV Feeder-11kV-3C-AG (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 11kV 3C AG (Outdoor)
|  |  |  | System Nominal Voltage |  |  | 11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  | 0.532
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  | 240
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 8.75 / 15 kV |  |  | Installation |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  | 55
[10 empty] | Number of Cores |  |  | 3C |  |  | Base Temperature (U/G) |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 6 | 6
[5 empty] | Size (mm2) | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 307 | 352 | 397 | 453 | 529 | 794 | 906 | 1058 | 1359 | 1587 | 2718 | 3174
Resistance (ohm/km) | [5 empty] | 0.247 | 0.196 | 0.159 | 0.1279 | 0.0982 | 0.0795 | 0.06395 | 0.0491 | 0.042633 | 0.032733 | 0.021317 | 0.016367
Reactance (ohm/km) | [5 empty] | 0.11 | 0.105 | 0.102 | 0.098 | 0.094 | 0.051 | 0.049 | 0.047 | 0.032667 | 0.031333 | 0.016333 | 0.015667
Derated Ampacity (A) | [5 empty] | 163.324 | 187.264 | 211.204 | 240.996 | 281.428 | 422.408 | 481.992 | 562.856 | 722.988 | 844.284 | 1445.976 | 1688.568 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 16000 | 839.7822 | 85 | 100 | 240 | [9 empty] | 1705.9865 | 2829.9291 | 3411.9729
| 27500 | 1443.3757 | 85 | 100 | 185 | [10 empty] | 1646.5042 | 1985.1479

## MV Feeder-11kV-3C-AG Indoor (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 11kV 3C AG (Indoor)
|  |  |  | System Nominal Voltage |  |  | 11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  | 0.609
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  | 240
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 8.75 / 15 kV |  |  | Installation |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  | 45
[10 empty] | Number of Cores |  |  | 3C |  |  | Base Temperature (U/G) |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 6 | 6
[5 empty] | Size (mm2) | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 307 | 352 | 397 | 453 | 529 | 794 | 906 | 1058 | 1359 | 1587 | 2718 | 3174
Resistance (ohm/km) | [5 empty] | 0.247 | 0.196 | 0.159 | 0.1279 | 0.0982 | 0.0795 | 0.06395 | 0.0491 | 0.042633 | 0.032733 | 0.021317 | 0.016367
Reactance (ohm/km) | [5 empty] | 0.11 | 0.105 | 0.102 | 0.098 | 0.094 | 0.051 | 0.049 | 0.047 | 0.032667 | 0.031333 | 0.016333 | 0.015667
Derated Ampacity (A) | [5 empty] | 186.963 | 214.368 | 241.773 | 275.877 | 322.161 | 483.546 | 551.754 | 644.322 | 827.631 | 966.483 | 1655.262 | 1932.966 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 2500 | 131.216 | 89.5 | 100 | 240 |  |  |  |  | 3728.2616 | 5154.3168 | 6119.4179 | 7456.5232 | 9179.1268 | 11184.7848 | 18358.2536 | 22369.5695
| 27500 | 1443.3757 | 85 | 100 | 185 | [10 empty] | 1646.5042 | 1985.1479

## MV Feeder-11 kV-1C-AG (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 11 kV 1C AG (Outdoor)
|  |  |  | System Nominal Voltage |  |  | 11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  | 0.654
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  | 400
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 8.75 / 15 kV |  |  | Installation |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  | 55
[10 empty] | Number of Cores |  |  | 1C |  |  | Base Temperature (U/G) |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 4
[5 empty] | Size | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400
Nominal Ampacity (A) | [5 empty] | 647 | 739 | 837 | 1294 | 1478 | 1674 | 1941 | 2217 | 2511 | 2588 | 2956 | 3348
Resistance (ohm/km) | [5 empty] | 0.0976 | 0.0785 | 0.0624 | 0.0488 | 0.03925 | 0.0312 | 0.032533 | 0.026167 | 0.0208 | 0.0244 | 0.019625 | 0.0156
Reactance (ohm/km) | [5 empty] | 0.185 | 0.18 | 0.173 | 0.0925 | 0.09 | 0.0865 | 0.061667 | 0.06 | 0.057667 | 0.04625 | 0.045 | 0.04325
Derated Ampacity (A) | [5 empty] | 423.138 | 483.306 | 547.398 | 846.276 | 966.612 | 1094.796 | 1269.414 | 1449.918 | 1642.194 | 1692.552 | 1933.224 | 2189.592 |  | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 16000 | 839.7822 | 85 | 100 | 240 |  |  |  | 838.3459 | 936.2665 | 1049.0839 | 1257.5188 | 1404.3998 | 1573.6259 | 1676.6917 | 1872.533 | 2098.1678
| 27500 | 1443.3757 | 85 | 100 | 185 | [7 empty] | 817.1053 | 915.5641 | 975.5297 | 1089.4738 | 1220.7522

## MV Feeder-11 kV-1C-AG Indoor (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 11 kV 1C AG (Indoor)
|  |  |  | System Nominal Voltage |  |  | 11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  | 0.748
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  | 400
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 8.75 / 15 kV |  |  | Installation |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  | 45
[10 empty] | Number of Cores |  |  | 1C |  |  | Base Temperature (U/G) |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 4
[5 empty] | Size | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400
Nominal Ampacity (A) | [5 empty] | 647 | 739 | 837 | 1294 | 1478 | 1674 | 1941 | 2217 | 2511 | 2588 | 2956 | 3348
Resistance (ohm/km) | [5 empty] | 0.0976 | 0.0785 | 0.0624 | 0.0488 | 0.03925 | 0.0312 | 0.032533 | 0.026167 | 0.0208 | 0.0244 | 0.019625 | 0.0156
Reactance (ohm/km) | [5 empty] | 0.185 | 0.18 | 0.173 | 0.0925 | 0.09 | 0.0865 | 0.061667 | 0.06 | 0.057667 | 0.04625 | 0.045 | 0.04325
Derated Ampacity (A) | [5 empty] | 483.956 | 552.772 | 626.076 | 967.912 | 1105.544 | 1252.152 | 1451.868 | 1658.316 | 1878.228 | 1935.824 | 2211.088 | 2504.304 |  | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 2500 | 131.216 | 89.5 | 100 | 240 | 2849.1666 | 3214.8915 | 3638.6206 | 5698.3332 | 6429.783 | 7277.2411 | 8547.4998 | 9644.6745 | 10915.8617 | 11396.6664 | 12859.5659 | 14554.4823
| 27500 | 1443.3757 | 85 | 100 | 185 | [6 empty] | 731.6473 | 817.1053 | 915.5641 | 975.5297 | 1089.4738 | 1220.7522

## MV Feeder-11kV-3C-UG (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 11kV 3C UG (Outdoor)
|  |  |  | System Nominal Voltage |  |  | 11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.496
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 8.75 / 15 kV |  |  | Installation |  |  | U/G
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 55
[10 empty] | Number of Cores |  |  | 3C |  |  | Base Temperature (U/G) |  |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3
[5 empty] | Size | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 129 | 154 | 181 | 220 | 263 | 298 | 332 | 374 | 431 | 664 | 748 | 862 | 1122 | 1293
Resistance (ohm/km) | [5 empty] | 0.927 | 0.668 | 0.494 | 0.342 | 0.247 | 0.196 | 0.159 | 0.1279 | 0.0961 | 0.0795 | 0.06395 | 0.04805 | 0.042633 | 0.032033
Reactance (ohm/km) | [5 empty] | 0.138 | 0.131 | 0.122 | 0.115 | 0.11 | 0.105 | 0.102 | 0.098 | 0.088 | 0.051 | 0.049 | 0.044 | 0.032667 | 0.029333
Derated Ampacity (A) | [5 empty] | 63.984 | 76.384 | 89.776 | 109.12 | 130.448 | 147.808 | 164.672 | 185.504 | 213.776 | 329.344 | 371.008 | 427.552 | 556.512 | 641.328 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 2500 | 131.216 | 85 | 100 | 185 | [7 empty] | 3018.5911 | 3780.0133 | 5124.8973 | 6037.1822 | 7560.0267 | 9055.7733 | 11340.04

## MV Motor-11kV-3C-UG (hidden)
CABLE SIZE SELECTION TABLE MOTOR FEEDER
MV Motor 11kV 3C UG (Outdoor)
|  | System Nominal Voltage |  |  | 11 | (kV) |  |  |  | A/G | Standard |  | IEC |  | Derating factor |  | 0.496
|  | Number of Phase |  |  | 3 | Ph |  |  |  | U/G | Unit System |  | Metric |  | Min Cable Size |  | Refer to Min. CSA
|  | System Frequency |  |  | 50 | (Hz) |  |  |  |  | Conductor Type |  | Cu |  | Max Cable Size |  | 240
|  | Voltage Drop @Running |  |  | 5 | (%) |  |  |  |  | Rated Voltage |  | 8.75 / 15 kV |  | Installation |  | U/G
|  | Voltage Drop @Starting |  |  | 15 | (%) |  |  |  |  | Insulation Type |  | XLPE/SWA/PVC |  | Base Temperature (A/G) |  | 55
|  | Wiring System |  |  | 3ph-3W | [5 empty] | Number of Cores |  | 3C |  | Base Temperature (U/G) |  | 30
[11 empty] | Max Conductor Temp. |  | 90
Cable Size | [6 empty] | Run |  |  |  | 1 | 1 |  | 1 | 1 | 1 | 3 |  | 2 |  | 5 |  | 10
[7 empty] | Size (mm2) |  |  |  | 95 | 120 |  | 150 | 185 | 240 | 95 |  | 185 |  | 240 |  | 240
Nominal Ampacity (A) | [10 empty] | 263 | 298 |  | 332 | 374 | 431 | 789 |  | 748 |  | 2155 |  | 4310
Resistance (ohm/km) | [10 empty] | 0.247 | 0.196 |  | 0.159 | 0.1279 | 0.0982 | 0.082333 |  | 0.06395 |  | 0.01964 |  | 0.00982
Reactance (ohm/km) | [10 empty] | 0.11 | 0.105 |  | 0.102 | 0.098 | 0.094 | 0.036667 |  | 0.049 |  | 0.0188 |  | 0.0094
Derated Ampacity (A) (=Nominal Ampacity x Total Derating Factor) | [10 empty] | 130.448 | 147.808 |  | 164.672 | 185.504 | 213.776 | 391.344 |  | 371.008 |  | 1068.88 |  | 2137.76 |  | 0
Output | Full Load |  | SF | MF | Eff. (%) | Locked Rotor |  | Min. | RL | XL | Maximum Cable Run (m)
kW | A | PF (%) |  |  |  | % | PF (%) | CSA
5700 | 341.3924 | 91 | 1 | 1 | 96.3 | 100 | 91 | 185 | 16.9285 | 7.7129 | [6 empty] | 10320.4791 | 36425.0211 | 11847.3587 | 41649.2309 | 36238.6904 | 126751.1445 | 72477.3807 | 253502.289
16030 | 981.0551 | 87.6 | 1 | 1 | 97.9 | 100 | 97.5 | 185 | 6.3117 | 1.4384 | [10 empty] | 12320.0948 | 47721.0848 | 24640.1895 | 95442.1696
30450 | 1620.9032 | 100 | 1 | 1 | 98.6 | 100 | 100 | 185 | 3.9181 | 0 | [12 empty] | 19949.5684 | 66123.2356
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0! | [10 empty] | 7
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
Note : | SF and MF is using for running voltage drop.
Note : | For each cross section, the first cell shows the Max. length due to normal running, and the next cell shows Max. length due to Starting
The minimum number is Bold.

## MV Motor-11kV-1C-UG (hidden)
CABLE SIZE SELECTION TABLE MOTOR FEEDER
MV Motor 11kV 1C UG (Outdoor)
|  | System Nominal Voltage |  |  | 11 | (kV) |  |  |  | A/G | Standard |  | IEC |  | Derating factor |  |  |  | 0.382
|  | Number of Phase |  |  | 3 | Ph |  |  |  | U/G | Unit System |  | Metric |  | Min Cable Size |  |  |  | Refer to Min. CSA
|  | System Frequency |  |  | 50 | (Hz) |  |  |  |  | Conductor Type |  | Cu |  | Max Cable Size |  |  |  | 400
|  | Voltage Drop @Running |  |  | 5 | (%) |  |  |  |  | Rated Voltage |  | 8.75 / 15 kV |  | Installation |  |  |  | U/G
|  | Voltage Drop @Starting |  |  | 15 | (%) |  |  |  |  | Insulation Type |  | XLPE/SWA/PVC |  | Base Temperature (A/G) |  |  |  | 55
|  | Wiring System |  |  | 3ph-3W | [5 empty] | Number of Cores |  | 1C |  | Base Temperature (U/G) |  |  |  | 30 | [14 empty] | `
[11 empty] | Max Conductor Temp. |  | 90
Cable Size | [6 empty] | Run |  |  |  | 1 | 1 |  | 1 | 2 |  | 2 |  | 3 |  | 3 |  | 4 |  | 4 |  | 5 |  | 5 |  | 9 |  | 10 |  | 10
[7 empty] | Size (mm2) |  |  |  | 240 | 300 |  | 400 | 240 |  | 300 |  | 300 |  | 400 |  | 300 |  | 400 |  | 300 |  | 400 |  | 400 |  | 300 |  | 400
Nominal Ampacity (A) | [10 empty] | 470 | 524 |  | 572 | 940 |  | 1048 |  | 1572 |  | 1716 |  | 2096 |  | 2288 |  | 2620 |  | 2860 |  | 5148 |  | 5240 |  | 5720
Resistance (ohm/km) | [10 empty] | 0.0971 | 0.0778 |  | 0.0614 | 0.04855 |  | 0.0389 |  | 0.025933 |  | 0.020467 |  | 0.01945 |  | 0.01535 |  | 0.01556 |  | 0.01228 |  | 0.0068222 |  | 0.00778 |  | 0.00614
Reactance (ohm/km) | [10 empty] | 0.189 | 0.184 |  | 0.178 | 0.0945 |  | 0.092 |  | 0.061333 |  | 0.059333 |  | 0.046 |  | 0.0445 |  | 0.0368 |  | 0.0356 |  | 0.019778 |  | 0.0184 |  | 0.0178
Derated Ampacity (A) (=Nominal Ampacity x Total Derating Factor) | [10 empty] | 179.54 | 200.168 |  | 218.504 | 359.08 |  | 400.336 |  | 600.504 |  | 655.512 |  | 800.672 |  | 874.016 |  | 1000.84 |  | 1092.52 |  | 1966.536 |  | 2001.68 |  | 2185.04 |  | 0
Output | Full Load |  | SF | MF | Eff. (%) | Locked Rotor |  | Min. | RL | XL | Maximum Cable Run (m)
kW | A | PF (%) |  |  |  | % | PF (%) | CSA
5700 | 341.3924 | 91 | 1 | 1 | 96.3 | 100 | 91 | 185 | 16.9285 | 7.7129 |  |  |  |  | 11157.9751 | 37686.9358 | 12647.5702 | 42110.9587 | 18971.3553 | 63166.438 | 21518.681 | 70481.3163 | 25295.1404 | 84221.9174 | 28691.5746 | 93975.0883 | 31618.9256 | 105277.3967 | 35864.4683 | 117468.8604 | 64556.0429 | 211443.9488 | 63237.8511 | 210554.7935 | 71728.9366 | 234937.7208
16030 | 981.0551 | 87.6 | 1 | 1 | 97.9 | 100 | 87.6 | 185 | 5.6708 | 3.1222 | [16 empty] | 10314.8075 | 34846.2542 | 11589.7944 | 38654.1843 | 20861.6299 | 69577.5317 | 20629.615 | 69692.5083 | 23179.5887 | 77308.3685
30450 | 1620.9032 | 100 | 1 | 1 | 98.6 | 100 | 100 | 185 | 3.9181 | 0 | [20 empty] | 28715.6817 | 70080.8321 | 25180.5607 | 67174.9927 | 31906.313 | 77867.5912
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
Note : | SF and MF is using for running voltage drop.
Note : | For each cross section, the first cell shows the Max. length due to normal running, and the next cell shows Max. length due to Starting
The minimum number is Bold.

## MV Feeder-33kV-1C-AG (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 33kV 1C AG (Outdoor)
|  |  |  | System Nominal Voltage |  |  | 33 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.756
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 800
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 18 / 30 kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 48
[10 empty] | Number of Cores |  |  | 1C |  |  | Base Temperature (U/G) |  |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4
[5 empty] | Size | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400
Nominal Ampacity (A) | [5 empty] | 745 | 846 | 938 | 1490 | 1692 | 1876 | 2235 | 2538 | 3752
Resistance (ohm/km) | [5 empty] | 0.097 | 0.778 | 0.614 | 0.0485 | 0.389 | 0.307 | 0.032333 | 0.25933 | 0.1535
Reactance (ohm/km) | [5 empty] | 0.196 | 0.19 | 0.183 | 0.098 | 0.095 | 0.0915 | 0.065333 | 0.063333 | 0.04575
Derated Ampacity (A) | [5 empty] | 563.22 | 639.576 | 709.128 | 1126.44 | 1279.152 | 1418.256 | 1689.66 | 1918.728 | 2836.512 | 0 | 0 | 0 | 0 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 19000 | 332.4138 | 85 | 100 | 150 | 3086.4821 | 752.7796 | 926.9881 | 6172.9642 | 1505.5592 | 1853.9762 | 9259.4463 | 2258.3388 | 3707.9525
| 47100 | 824.0363 | 85 | 100 | 150 |  |  |  | 2490.1554 | 607.3381 | 747.8885 | 3735.2331 | 911.0072 | 1495.777
| 53500 | 936.0073 | 85 | 100 | 150 |  |  |  | 2192.2677 | 534.6846 | 658.4215 | 3288.4015 | 802.0269 | 1316.8429
| 132000 | 2309.4011 | 85 | 100 | 185 | [8 empty] | 533.7204

## MV Feeder-33kV-1C-UG (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 33kV 1C UG (Outdoor)
|  |  |  | System Nominal Voltage |  |  | 33 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.593
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 800
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 18 / 30 kV |  |  | Installation |  |  | U/G
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 48
[10 empty] | Number of Cores |  |  | 1C |  |  | Base Temperature (U/G) |  |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 7
[5 empty] | Size | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400
Nominal Ampacity (A) | [5 empty] | 470 | 524 | 572 | 940 | 1048 | 1144 | 1410 | 1572 | 4004
Resistance (ohm/km) | [5 empty] | 0.247 | 0.196 | 0.159 | 0.1235 | 0.098 | 0.0795 | 0.082333 | 0.065333 | 0.022714
Reactance (ohm/km) | [5 empty] | 0.13 | 0.124 | 0.12 | 0.065 | 0.062 | 0.06 | 0.043333 | 0.041333 | 0.017143
Derated Ampacity (A) | [5 empty] | 278.71 | 310.732 | 339.196 | 557.42 | 621.464 | 678.392 | 836.13 | 932.196 | 2374.372 | 0 | 0 | 0 | 0 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 19000 | 332.4138 | 85 | 100 | 150 |  |  | 2889.4261 | 4117.0441 | 4942.6983 | 5778.8522 | 6175.5661 | 7414.0474 | 20225.9827
| 47100 | 824.0363 | 85 | 100 | 150 | [6 empty] | 2491.205 | 2990.8047 | 8159.1013
| 53500 | 936.0073 | 85 | 100 | 150 | [8 empty] | 7183.0593
| 132000 | 2309.4011 | 85 | 100 | 185 | [8 empty] | 2911.3157

## MV Motor-6kV-3C-AG (hidden)
CABLE SIZE SELECTION TABLE MOTOR FEEDER
MV Motor 6kV 3C AG (Outdoor)
|  | System Nominal Voltage |  |  | 6 | (kV) |  |  |  | A/G | Standard |  | IEC |  | Derating factor |  | 0.628
|  | Number of Phase |  |  | 3 | Ph |  |  |  | U/G | Unit System |  | Metric |  | Min Cable Size |  | Refer to Min. CSA
|  | System Frequency |  |  | 50 | (Hz) |  |  |  |  | Conductor Type |  | Cu |  | Max Cable Size |  | 240
|  | Voltage Drop @Running |  |  | 3.25 | (%) |  |  |  |  | Rated Voltage |  | 3.6 / 6 kV |  | Installation |  | A/G
|  | Voltage Drop @Starting |  |  | 15 | (%) |  |  |  |  | Insulation Type |  | XLPE/SWA/PVC |  | Base Temperature (A/G) |  | 52
|  | Wiring System |  |  | 3ph-3W | [5 empty] | Number of Cores |  | 3C |  | Base Temperature (U/G) |  | 35 | [14 empty] | `
[11 empty] | Max Conductor Temp. |  | 90
Cable Size | [6 empty] | Run |  |  |  | 1 | 1 |  | 1 | 1 | 1 | 1 |  | 1 |  | 1 |  | 1 |  | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 3 |  | 3 |  | 3 |  | 4
[7 empty] | Size (mm2) |  |  |  | 25 | 35 |  | 50 | 70 | 95 | 120 |  | 150 |  | 185 |  | 240 |  | 95 |  | 120 |  | 150 |  | 185 |  | 240 |  | 120 |  | 150 |  | 185 |  | 150
Nominal Ampacity (A) | [10 empty] | 143 | 172 |  | 205 | 253 | 307 | 352 |  | 397 |  | 453 |  | 529 |  | 614 |  | 704 |  | 794 |  | 906 |  | 1058 |  | 1056 |  | 1191 |  | 1359 |  | 1588
Resistance (ohm/km) | [10 empty] | 0.927 | 0.668 |  | 0.494 | 0.342 | 0.247 | 0.196 |  | 0.159 |  | 0.1279 |  | 0.0961 |  | 0.1235 |  | 0.098 |  | 0.0795 |  | 0.06395 |  | 0.04805 |  | 0.065333 |  | 0.053 |  | 0.042633 |  | 0.03975
Reactance (ohm/km) | [10 empty] | 0.138 | 0.131 |  | 0.122 | 0.115 | 0.11 | 0.105 |  | 0.102 |  | 0.098 |  | 0.088 |  | 0.055 |  | 0.0525 |  | 0.051 |  | 0.049 |  | 0.044 |  | 0.035 |  | 0.034 |  | 0.032667 |  | 0.0255
Derated Ampacity (A) (=Nominal Ampacity x Total Derating Factor) | [10 empty] | 89.804 | 108.016 |  | 128.74 | 158.884 | 192.796 | 221.056 |  | 249.316 |  | 284.484 |  | 332.212 |  | 385.592 |  | 442.112 |  | 498.632 |  | 568.968 |  | 664.424 |  | 663.168 |  | 747.948 |  | 853.452 |  | 997.264
Output | Full Load |  | SF | MF | Eff. (%) | Locked Rotor |  | Min. | RL | XL | Maximum Cable Run (m)
kW | A | PF (%) |  |  |  | % | PF (%) | CSA
1800 | 206.5871 | 87.7 | 1 | 1 | 95.6 | 600 | 16 | 120 | 0.44715 | 2.7587 | [6 empty] | 2451.0176 | 3273.3292 | 2891.7966 | 3599.4459 | 3421.9532 | 3958.3248 | 4305.9064 | 4616.174 | 4044.694 | 5774.9725 | 4902.0351 | 6546.6583 | 5783.5932 | 7198.8918 | 6843.9064 | 7916.6495 | 8611.8128 | 9232.348 | 7353.0527 | 9819.9875 | 8675.3898 | 10798.3378 | 10265.8596 | 11874.9743 | 11567.1865 | 14397.7837
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
Note : | SF and MF is using for running voltage drop.
Note : | For each cross section, the first cell shows the Max. length due to normal running, and the next cell shows Max. length due to Starting
The minimum number is Bold.

## MV Motor-11kV-3C-UG
CABLE SIZE SELECTION TABLE MOTOR FEEDER
MV Motor 11kV 3C UG
|  | System Nominal Voltage |  |  | 11 | (kV) |  |  |  | A/G | Standard |  |  | IEC |  |  | Derating factor |  |  |  | 0.56
|  | Number of Phase |  |  | 3 | Ph |  |  |  | U/G | Unit System |  |  | Metric |  |  | Min Cable Size |  |  |  | Refer to Min. CSA
|  | System Frequency |  |  | 50 | (Hz) |  |  |  |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  |  | 240
|  | Voltage Drop @Running |  |  | 3.25 | (%) |  |  |  |  | Rated Voltage |  |  | 10/11 kv |  |  | Installation |  |  |  | U/G
|  | Voltage Drop @Starting |  |  | 15 | (%) |  |  |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  |  | 50
|  | Wiring System |  |  | 3ph-3W | [5 empty] | Number of Cores |  |  | 3C |  |  | Base Temperature (U/G) |  |  |  | 35
[11 empty] | Max Conductor Temp. |  |  | 90
Cable Size | [6 empty] | Run |  |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1
[7 empty] | Size (mm2) |  |  |  | 35 |  | 50 |  | 70 |  | 95 |  | 120 |  | 150 |  | 185 |  | 240 |  | 300
Nominal Ampacity (A) | [10 empty] | 154 |  | 181 |  | 220 |  | 263 |  | 298 |  | 332 |  | 374 |  | 431 |  | 482 |  | Page 54 of MV Cable Abhar
Resistance (ohm/km) | [10 empty] | 0.668 |  | 0.494 |  | 0.342 |  | 0.247 |  | 0.196 |  | 0.159 |  | 0.128 |  | 0.098 |  | 0.0791 |  | Page 26 of MV Cable Abhar
Reactance (ohm/km) | [10 empty] | 0.14 |  | 0.13 |  | 0.123 |  | 0.117 |  | 0.111 |  | 0.108 |  | 0.104 |  | 0.1 |  | 0.097
Derated Ampacity (A) (=Nominal Ampacity x Total Derating Factor) | [10 empty] | 86.24 |  | 101.36 |  | 123.2 |  | 147.28 |  | 166.88 |  | 185.92 |  | 209.44 |  | 241.36 |  | 269.92
Output | Full Load |  | SF | MF | Eff. (%) | Locked Rotor |  | Min. | RL | XL | Maximum Cable Run (m)
kW | A | PF (%) |  |  |  | % | PF (%) | CSA
1250 | 89.6897 | 77 | 1 | 1 | 95 | 600 | 40 | 95 | 4.7206 | 10.8163 | [6 empty] | 8689.3564 | 9588.0435 | 10378.2322 | 11109.0169 | 12027.3553 | 12448.0082 | 13954.323 | 13939.9572 | 16524.6767 | 15746.4321 | 18740.6385 | 17177.0357
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
Note : | SF and MF is using for running voltage drop.
Note : | For each cross section, the first cell shows the Max. length due to normal running, and the next cell shows Max. length due to Starting
The minimum number is Bold.

## MV Motor-3.3kV-3C-UG
CABLE SIZE SELECTION TABLE MOTOR FEEDER
MV Motor 3.3kV 3C UG
|  | System Nominal Voltage |  |  | 3.3 | (kV) |  |  |  | A/G | Standard |  |  | IEC |  |  | Derating factor |  |  |  | 0.56
|  | Number of Phase |  |  | 3 | Ph |  |  |  | U/G | Unit System |  |  | Metric |  |  | Min Cable Size |  |  |  | Refer to Min. CSA
|  | System Frequency |  |  | 50 | (Hz) |  |  |  |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  |  | 240
|  | Voltage Drop @Running |  |  | 3.25 | (%) |  |  |  |  | Rated Voltage |  |  | 3.3 kV |  |  | Installation |  |  |  | U/G
|  | Voltage Drop @Starting |  |  | 15 | (%) |  |  |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  |  | 50
|  | Wiring System |  |  | 3ph-3W | [5 empty] | Number of Cores |  |  | 3C |  |  | Base Temperature (U/G) |  |  |  | 35
[11 empty] | Max Conductor Temp. |  |  | 90
Cable Size | [6 empty] | Run |  |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1
[7 empty] | Size (mm2) |  |  |  | 25 |  | 35 |  | 50 |  | 70 |  | 95 |  | 120 |  | 150 |  | 185 |  | 240
Nominal Ampacity (A) | [10 empty] | 129 |  | 154 |  | 181 |  | 220 |  | 263 |  | 298 |  | 332 |  | 374 |  | 431 |  | Page 54 of MV Cable Abhar
Resistance (ohm/km) | [10 empty] | 0.927 |  | 0.668 |  | 0.494 |  | 0.342 |  | 0.247 |  | 0.196 |  | 0.159 |  | 0.128 |  | 0.0984 |  | Page 15 of MV Cable Abhar
Reactance (ohm/km) | [10 empty] | 0.132 |  | 0.126 |  | 0.117 |  | 0.111 |  | 0.105 |  | 0.101 |  | 0.098 |  | 0.095 |  | 0.091
Derated Ampacity (A) (=Nominal Ampacity x Total Derating Factor) | [10 empty] | 72.24 |  | 86.24 |  | 101.36 |  | 123.2 |  | 147.28 |  | 166.88 |  | 185.92 |  | 209.44 |  | 241.36
Output | Full Load |  | SF | MF | Eff. (%) | Locked Rotor |  | Min. | RL | XL | Maximum Cable Run (m)
kW | A | PF (%) |  |  |  | % | PF (%) | CSA
300 | 71.7517 | 77 | 1 | 1 | 95 | 600 | 40 | 50 | 1.7702 | 4.0561 |  |  |  |  | 1896.5452 | 2288.0193 | 2582.5344 | 3008.6897 | 3355.5162 | 3765.8875 | 4007.1386 | 4360.2691 | 4665.847 | 4918.2863 | 5421.6531 | 5515.1646 | 6448.3835 | 6272.5956
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[12 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
[9 empty] | #DIV/0! | #DIV/0!
Note : | SF and MF is using for running voltage drop.
Note : | For each cross section, the first cell shows the Max. length due to normal running, and the next cell shows Max. length due to Starting
The minimum number is Bold.

## MV Feeder-6kV-3C-UG (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 6kV 3C UG (Outdoor)
|  |  |  | System Nominal Voltage |  |  | 6 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.628
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 3.6 / 6 kV |  |  | Installation |  |  | U/G
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 48
[10 empty] | Number of Cores |  |  | 3C |  |  | Base Temperature (U/G) |  |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 9
[5 empty] | Size | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240 | 240
Nominal Ampacity (A) | [5 empty] | 129 | 154 | 181 | 220 | 263 | 298 | 332 | 374 | 431 | 664 | 748 | 862 | 1122 | 1293 | 3879
Resistance (ohm/km) | [5 empty] | 0.927 | 0.668 | 0.494 | 0.342 | 0.247 | 0.196 | 0.159 | 0.1279 | 0.0961 | 0.0795 | 0.06395 | 0.04805 | 0.042633 | 0.032033 | 0.010678
Reactance (ohm/km) | [5 empty] | 0.138 | 0.131 | 0.122 | 0.115 | 0.11 | 0.105 | 0.102 | 0.098 | 0.088 | 0.051 | 0.049 | 0.044 | 0.032667 | 0.029333 | 0.0097778
Derated Ampacity (A) | [5 empty] | 81.012 | 96.712 | 113.668 | 138.16 | 165.164 | 187.144 | 208.496 | 234.872 | 270.668 | 416.992 | 469.744 | 541.336 | 704.616 | 812.004 | 2436.012
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 2500 | 240.5626 | 85 | 100 | 120 | [8 empty] | 1124.6321 | 1524.7628 | 1796.1864 | 2249.2641 | 2694.2797 | 3373.8962 | 10121.6886
| 19000 | 1828.2759 | 85 | 100 | 185 | [14 empty] | 1331.8011

## MV Feeder_6kV_1C_AG (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 6kV 1C AG (Outdoor)
|  |  |  | System Nominal Voltage |  |  | 6 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  | 0.756
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  | 400
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 3.6 / 6 kV |  |  | Installation |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/AWA/PVC |  |  | Base Temperature (A/G) |  | 48
[10 empty] | Number of Cores |  |  | 1C |  |  | Base Temperature (U/G) |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 7 | 8
[5 empty] | Size | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 300 | 300 | 400
Nominal Ampacity (A) | [5 empty] | 641 | 735 | 845 | 1282 | 1470 | 1690 | 1923 | 2205 | 2205 | 5145 | 6760
Resistance (ohm/km) | [5 empty] | 0.0976 | 0.0785 | 0.0624 | 0.0488 | 0.03925 | 0.0312 | 0.032533 | 0.026167 | 0.026167 | 0.011214 | 0.0078
Reactance (ohm/km) | [5 empty] | 0.185 | 0.18 | 0.173 | 0.0925 | 0.09 | 0.0865 | 0.061667 | 0.06 | 0.06 | 0.025714 | 0.021625
Derated Ampacity (A) | [5 empty] | 484.596 | 555.66 | 638.82 | 969.192 | 1111.32 | 1277.64 | 1453.788 | 1666.98 | 1666.98 | 3889.62 | 5110.56 | 0 |  | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 19000 | 1828.2759 | 85 | 100 | 120 | [9 empty] | 821.0149 | 1051.3655
| 2500 | 240.5626 | 85 | 100 | 120 | 798.1607 | 891.3876 | 998.7972 | 1596.3214 | 1782.7752 | 1997.5945 | 2394.4821 | 2674.1628 | 2674.1628 | 6239.7133 | 7990.378

## MV Feeder_6kV_1C_UG (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 6kV 1C UG (Outdoor)
|  |  |  | System Nominal Voltage |  |  | 6 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  | 0.593
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  | 400
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 3.6 / 6 kV |  |  | Installation |  | U/G
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/AWA/PVC |  |  | Base Temperature (A/G) |  | 48
[10 empty] | Number of Cores |  |  | 1C |  |  | Base Temperature (U/G) |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 7 | 8
[5 empty] | Size | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 300 | 300 | 400
Nominal Ampacity (A) | [5 empty] | 470 | 524 | 572 | 940 | 1048 | 1144 | 1410 | 1572 | 1572 | 3668 | 4576
Resistance (ohm/km) | [5 empty] | 0.0976 | 0.0785 | 0.0624 | 0.0488 | 0.03925 | 0.0312 | 0.032533 | 0.026167 | 0.026167 | 0.011214 | 0.0078
Reactance (ohm/km) | [5 empty] | 0.185 | 0.18 | 0.173 | 0.0925 | 0.09 | 0.0865 | 0.061667 | 0.06 | 0.06 | 0.025714 | 0.021625
Derated Ampacity (A) | [5 empty] | 278.71 | 310.732 | 339.196 | 557.42 | 621.464 | 678.392 | 836.13 | 932.196 | 932.196 | 2175.124 | 2713.568 | 0 |  | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 19000 | 1828.2759 | 85 | 100 | 120 | [9 empty] | 821.0149 | 1051.3655
| 2500 | 240.5626 | 85 | 100 | 120 | 798.1607 | 891.3876 | 998.7972 | 1596.3214 | 1782.7752 | 1997.5945 | 2394.4821 | 2674.1628 | 2674.1628 | 6239.7133 | 7990.378

## MV Feeder-6kV-3C-AG (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 6kV 3C AG (Outdoor)
|  |  |  | System Nominal Voltage |  |  | 6 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.78
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 3.6 / 6 kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 48
[10 empty] | Number of Cores |  |  | 3C |  |  | Base Temperature (U/G) |  |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 5
[5 empty] | Size (mm2) | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240 | 240
Nominal Ampacity (A) | [5 empty] | 143 | 172 | 205 | 253 | 307 | 352 | 397 | 453 | 529 | 794 | 906 | 1058 | 1359 | 1587 | 2645
Resistance (ohm/km) | [5 empty] | 0.927 | 0.668 | 0.494 | 0.342 | 0.247 | 0.196 | 0.159 | 0.1279 | 0.0961 | 0.0795 | 0.06395 | 0.04805 | 0.042633 | 0.032033 | 0.01922
Reactance (ohm/km) | [5 empty] | 0.138 | 0.131 | 0.122 | 0.115 | 0.11 | 0.105 | 0.102 | 0.098 | 0.088 | 0.051 | 0.049 | 0.044 | 0.032667 | 0.029333 | 0.0176
Derated Ampacity (A) | [5 empty] | 111.54 | 134.16 | 159.9 | 197.34 | 239.46 | 274.56 | 309.66 | 353.34 | 412.62 | 619.32 | 706.68 | 825.24 | 1060.02 | 1237.86 | 2063.1
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 19000 | 1828.2759 | 85 | 100 | 185 | [14 empty] | 739.8895
| 2500 | 240.5626 | 85 | 100 | 185 | [7 empty] | 898.0932 | 1124.6321 | 1524.7628 | 1796.1864 | 2249.2641 | 2694.2797 | 3373.8962 | 5623.1603

## MV Feeder-6kV-3C-AG Indoor (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 6kV 3C AG (Indoor)
|  |  |  | System Nominal Voltage |  |  | 6 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.609
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 3.6 / 6 kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 45
[10 empty] | Number of Cores |  |  | 3C |  |  | Base Temperature (U/G) |  |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3
[5 empty] | Size (mm2) | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 143 | 172 | 205 | 253 | 307 | 352 | 397 | 453 | 529 | 794 | 906 | 1058 | 1359 | 1587
Resistance (ohm/km) | [5 empty] | 0.927 | 0.668 | 0.494 | 0.342 | 0.247 | 0.196 | 0.159 | 0.1279 | 0.0961 | 0.0795 | 0.06395 | 0.04805 | 0.042633 | 0.032033
Reactance (ohm/km) | [5 empty] | 0.138 | 0.131 | 0.122 | 0.115 | 0.11 | 0.105 | 0.102 | 0.098 | 0.088 | 0.051 | 0.049 | 0.044 | 0.032667 | 0.029333
Derated Ampacity (A) | [5 empty] | 87.087 | 104.748 | 124.845 | 154.077 | 186.963 | 214.368 | 241.773 | 275.877 | 322.161 | 483.546 | 551.754 | 644.322 | 827.631 | 966.483 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 1600 | 153.9601 | 85 | 100 | 185 | [7 empty] | 1403.2707 | 1757.2376 | 2382.4419 | 2806.5413 | 3514.4752 | 4209.812 | 5271.7128
| 2000 | 192.4501 | 85 | 100 | 185 | [7 empty] | 1122.6165 | 1405.7901 | 1905.9535 | 2245.233 | 2811.5802 | 3367.8496 | 4217.3702
| 2500 | 240.5626 | 85 | 100 | 185 | [7 empty] | 898.0932 | 1124.6321 | 1524.7628 | 1796.1864 | 2249.2641 | 2694.2797 | 3373.8962
| 3150 | 303.1089 | 85 | 100 | 185 | [8 empty] | 892.5651 | 1210.1292 | 1425.5448 | 1785.1303 | 2138.3172 | 2677.6954

## MV Feeder-6 kV-1C-AG indr (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
MV Feeder 6 kV 1C AG (Indoor)
|  |  |  | System Nominal Voltage |  |  | 6 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  | 0.748
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  | 400
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 3.6 / 6 kV |  |  | Installation |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  | 45
[10 empty] | Number of Cores |  |  | 1C |  |  | Base Temperature (U/G) |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 4
[5 empty] | Size | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400
Nominal Ampacity (A) | [5 empty] | 647 | 739 | 837 | 1294 | 1478 | 1674 | 1941 | 2217 | 2511 | 2588 | 2956 | 3348
Resistance (ohm/km) | [5 empty] | 0.0971 | 0.0778 | 0.0614 | 0.04855 | 0.0389 | 0.0307 | 0.032367 | 0.025933 | 0.020467 | 0.024275 | 0.01945 | 0.01535
Reactance (ohm/km) | [5 empty] | 0.189 | 0.184 | 0.178 | 0.0945 | 0.092 | 0.089 | 0.063 | 0.061333 | 0.059333 | 0.04725 | 0.046 | 0.0445
Derated Ampacity (A) | [5 empty] | 483.956 | 552.772 | 626.076 | 967.912 | 1105.544 | 1252.152 | 1451.868 | 1658.316 | 1878.228 | 1935.824 | 2211.088 | 2504.304 |  | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 1600 | 153.9601 | 89.5 | 100 | 185 | 1314.1679 | 1483.1204 | 1674.6956 | 2628.3358 | 2966.2408 | 3349.3912 | 3942.5037 | 4449.3612 | 5024.0869 | 5256.6716 | 5932.4817 | 6698.7825
| 2000 | 192.4501 | 85 | 100 | 185 | 988.4846 | 1103.9016 | 1233.2372 | 1976.9691 | 2207.8032 | 2466.4745 | 2965.4537 | 3311.7047 | 3699.7117 | 3953.9382 | 4415.6063 | 4932.9489
| 2500 | 240.5626 | 85 | 100 | 185 | 790.7876 | 883.1213 | 986.5898 | 1581.5753 | 1766.2425 | 1973.1796 | 2372.3629 | 2649.3638 | 2959.7694 | 3163.1506 | 3532.4851 | 3946.3592
| 3150 | 303.1089 | 85 | 100 | 185 | 627.6092 | 700.8899 | 783.0078 | 1255.2185 | 1401.7798 | 1566.0155 | 1882.8277 | 2102.6697 | 2349.0233 | 2510.437 | 2803.5596 | 3132.0311

## LV Motor_3C_AG (hidden)
CABLE SIZE SELECTION TABLE MOTOR FEEDER
LV Motor 3C AG (Outdoor)
|  | System Nominal Voltage |  |  | 0.4 | (kV) |  |  | A/G | Standard |  | IEC |  |  | Derating factor |  |  |  | 0.533
|  | Number of Phase |  |  | 3 | Ph |  |  | U/G | Unit System |  | Metric |  |  | Min Cable Size |  |  |  | 4
|  | System Frequency |  |  | 50 | (Hz) |  |  |  | Conductor Type |  | Cu |  |  | Max Cable Size |  |  |  | 240
|  | Voltage Drop @Running |  |  | 5 | (%) |  |  |  | Rated Voltage |  | 0.6/1kV |  |  | Installation |  |  |  | A/G
|  | Voltage Drop @Starting |  |  | 15 | (%) |  |  |  | Insulation Type |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  |  | 48
|  | Wiring System |  |  | 3ph-3W |  |  |  |  | Number of Cores |  | 3C |  |  | Base Temperature (U/G) |  |  |  | 30
[10 empty] | Max Conductor Temp. |  | 90
Cable Size | [6 empty] | Run |  |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 2 |  | 2 |  | 2 |  | 3 |  | 3 |  | 2 |  | 3
[7 empty] | Size (mm2) |  |  |  | 4 |  | 6 |  | 10 |  | 16 |  | 25 |  | 35 |  | 50 |  | 70 |  | 95 |  | 120 |  | 150 |  | 185 |  | 240 |  | 120 |  | 150 |  | 240 |  | 150 |  | 240 |  | 185 |  | 150
Nominal Ampacity (A) | [10 empty] | 42 |  | 54 |  | 75 |  | 100 |  | 127 |  | 158 |  | 192 |  | 246 |  | 298 |  | 346 |  | 399 |  | 456 |  | 538 |  | 692 |  | 798 |  | 1076 |  | 1197 |  | 1614 |  | 912 |  | 1197
Resistance (ohm/km) | [10 empty] | 5.88 |  | 3.93 |  | 2.33 |  | 1.47 |  | 0.927 |  | 0.668 |  | 0.493 |  | 0.342 |  | 0.246 |  | 0.195 |  | 0.158 |  | 0.1264 |  | 0.0961 |  | 0.0975 |  | 0.079 |  | 0.04805 |  | 0.052667 |  | 0.032033 |  | 0.0632 |  | 0.052667
Reactance (ohm/km) | [10 empty] | 0.098 |  | 0.095 |  | 0.09 |  | 0.088 |  | 0.089 |  | 0.083 |  | 0.083 |  | 0.082 |  | 0.079 |  | 0.079 |  | 0.079 |  | 0.079 |  | 0.071 |  | 0.0395 |  | 0.0395 |  | 0.0355 |  | 0.026333 |  | 0.023667 |  | 0.0395 |  | 0.026333
Derated Ampacity (A) (=Nominal Ampacity x Total Derating Factor x Run) | [10 empty] | 22.386 |  | 28.782 |  | 39.975 |  | 53.3 |  | 67.691 |  | 84.214 |  | 102.336 |  | 131.118 |  | 158.834 |  | 184.418 |  | 212.667 |  | 243.048 |  | 286.754 |  | 368.836 |  | 425.334 |  | 573.508 |  | 638.001 |  | 860.262 |  | 486.096 |  | 638.001
Output | Full Load |  | SF | MF | Eff. (%) | Locked Rotor |  | RL | XL | Maximum Cable Run (m)
kW | A | PF (%) |  |  |  | % | PF (%)
0.6 | 1.0825 | 80 | 1 | 1 | 100 | 500 | 70 | 29.8667 | 30.4701 |  | 2239.579 | 1683.1446 | 3332.292 | 2503.9686 | 5561.3486 | 4177.4323 | 8680.5556 | 6516.2016 | 13417.1908 | 10057.7055 | 18258.5872 | 13668.7315 | 24013.2073 | 17933.3993 | 33044.1966 | 24564.255 | 43680.0437 | 32275.849 | 52441.8224 | 38489.4808 | 61373.2259 | 44687.1324 | 71819.7325 | 51738.7036 | 89275.7505 | 63699.7842 | 104883.6447 | 76978.9617 | 122746.4519 | 89374.2647 | 178551.5009 | 127399.5685 | 184119.6778 | 134061.3971 | 267827.2514 | 191099.3527 | 287278.9299 | 206954.8145 | 552359.0334 | 402184.1913
1.2 | 2.1651 | 80 | 1 | 1 | 100 | 700 | 50 | 7.619 | 13.1966 |  | 1119.7895 | 754.095 | 1666.146 | 1119.1574 | 2780.6743 | 1858.5712 | 4340.2778 | 2879.8717 | 6708.5954 | 4396.0688 | 9129.2936 | 5924.2526 | 12006.6036 | 7674.3007 | 16522.0983 | 10309.3177 | 21840.0218 | 13272.1295 | 26220.9112 | 15526.974 | 30686.613 | 17679.8611 | 35909.8662 | 20015.0269 | 44637.8752 | 24209.0463 | 52441.8224 | 31053.948 | 61373.2259 | 35359.7222 | 89275.7505 | 48418.0925 | 92059.8389 | 53039.5833 | 133913.6257 | 72627.1388 | 143639.4649 | 80060.1076 | 276179.5167 | 159118.7498
5 | 9.0211 | 80 | 1 | 1 | 100 | 700 | 40 | 1.4629 | 3.3518 |  | 268.7495 | 205.6945 | 399.875 | 304.9186 | 667.3618 | 505.2478 | 1041.6667 | 780.3417 | 1610.0629 | 1184.6823 | 2191.0305 | 1589.8323 | 2881.5849 | 2046.4034 | 3965.3036 | 2722.294 | 5241.6052 | 3468.866 | 6293.0187 | 4019.4664 | 7364.7871 | 4532.786 | 8618.3679 | 5075.2722 | 10713.0901 | 6086.4032 | 12586.0374 | 8038.9329 | 14729.5742 | 9065.572 | 21426.1801 | 12172.8063 | 22094.3613 | 13598.3581 | 32139.2702 | 18259.2095 | 34473.4716 | 20301.0888 | 66283.084 | 40795.0742
12 | 21.6506 | 80 | 1 | 1 | 100 | 735 | 35 | 0.50794 | 1.3595 |  | 111.9789 | 87.3502 | 166.6146 | 129.4146 | 278.0674 | 214.2086 | 434.0278 | 330.3166 | 670.8595 | 500.1283 | 912.9294 | 669.7745 | 1200.6604 | 859.3812 | 1652.2098 | 1137.5907 | 2184.0022 | 1442.0254 | 2622.0911 | 1662.766 | 3068.6613 | 1865.9117 | 3590.9866 | 2077.5755 | 4463.7875 | 2480.728 | 5244.1822 | 3325.5321 | 6137.3226 | 3731.8235 | 8927.575 | 4961.456 | 9205.9839 | 5597.7352 | 13391.3626 | 7442.184 | 14363.9465 | 8310.302 | 27617.9517 | 16793.2056
179 | 322.9553 | 80 |  |  | 100 |  |  | #DIV/0! | #DIV/0!
240 | 433.0127 | 80 |  |  | 100 |  |  | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
Note : | SF and MF is using for running voltage drop.
Note : | For each cross section, the first cell shows the Max. length due to normal running, and the next cell shows Max. length due to Starting
The minimum number is Bold.

## LV Motor_3C_UG
CABLE SIZE SELECTION TABLE MOTOR FEEDER
LV Motor 3C UG
|  | System Nominal Voltage |  |  | 0.4 | (kV) |  |  | A/G | Standard |  | IEC |  |  | Derating factor |  |  |  | 0.52
|  | Number of Phase |  |  | 3 | Ph |  |  | U/G | Unit System |  | Metric |  |  | Min Cable Size |  |  |  | 4
|  | System Frequency |  |  | 50 | (Hz) |  |  |  | Conductor Type |  | Cu |  |  | Max Cable Size |  |  |  | 240
|  | Voltage Drop @Running |  |  | 5 | (%) |  |  |  | Rated Voltage |  | 0.6/1kV |  |  | Installation |  |  |  | U/G
|  | Voltage Drop @Starting |  |  | 15 | (%) |  |  |  | Insulation Type |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  |  | 50
|  | Wiring System |  |  | 3ph-3W |  |  |  |  | Number of Cores |  | 3C |  |  | Base Temperature (U/G) |  |  |  | 35
[10 empty] | Max Conductor Temp. |  | 90
Cable Size | [6 empty] | Run |  |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | [6 empty] | 2 |  | 3
[7 empty] | Size (mm2) |  |  |  | 4 |  | 6 |  | 10 |  | 16 |  | 25 |  | 35 |  | 50 |  | 70 |  | 95 |  | 120 |  | 150 |  | 185 |  | 240 | [6 empty] | 185 |  | 150
Nominal Ampacity (A) | [10 empty] | 39 |  | 49 |  | 65 |  | 84 |  | 107 |  | 129 |  | 153 |  | 188 |  | 226 |  | 257 |  | 287 |  | 324 |  | 375 | [6 empty] | 648 |  | 861 |  | Installation type D2, page 46 of IEC60364
Resistance (ohm/km) | [10 empty] | 5.88 |  | 3.93 |  | 2.33 |  | 1.47 |  | 0.927 |  | 0.669 |  | 0.494 |  | 0.343 |  | 0.247 |  | 0.197 |  | 0.16 |  | 0.129 |  | 0.0996 | [6 empty] | 0.0645 |  | 0.053333 |  | Page 15 of LV Cable Abhar
Reactance (ohm/km) | [10 empty] | 0.09 |  | 0.087 |  | 0.083 |  | 0.081 |  | 0.081 |  | 0.079 |  | 0.075 |  | 0.075 |  | 0.072 |  | 0.072 |  | 0.072 |  | 0.072 |  | 0.071 | [6 empty] | 0.036 |  | 0.024
Derated Ampacity (A) (=Nominal Ampacity x Total Derating Factor x Run) | [10 empty] | 20.28 |  | 25.48 |  | 33.8 |  | 43.68 |  | 55.64 |  | 67.08 |  | 79.56 |  | 97.76 |  | 117.52 |  | 133.64 |  | 149.24 |  | 168.48 |  | 195 |  | 0 | 0 | 0 | 0 | 0 | 336.96 |  | 447.72
Output | Full Load |  | SF | MF | Eff. (%) | Locked Rotor |  | RL | XL | Maximum Cable Run (m)
kW | A | PF (%) |  |  |  | % | PF (%)
0.55 | 0.99232 | 80 | 1 | 1 | 100 | 4.6 | 70 | 3541.502 | 3613.0547 |  | 2445.6418 | 199789.0538 | 3640.687 | 297372.5989 | 6080.2402 | 496474.7923 | 9502.1751 | 775444.4196 | 14725.8462 | 1200297.9978 | 19973.1611 | 1625745.8191 | 26434.2654 | 2147852.3207 | 36431.9463 | 2948009.2491 | 48323.7693 | 3890019.0119 | 57950.0181 | 4638046.68 | 67969.4138 | 5402142.5264 | 79483.3582 | 6259480.4653 | 95161.6261 | 7396399.1851 | [5 empty] | 317933.4327 | 25037921.861 | 611724.7239 | 48619282.7372
1.1 | 2.3655 | 80 | 1 | 1 | 83.9 | 6.1 | 70 | 1120.3338 | 1142.9691 |  | 1025.9467 | 63202.1208 | 1527.2682 | 94072.1154 | 2550.6608 | 157056.9519 | 3986.1625 | 245307.3929 | 6177.4925 | 379707.3847 | 8378.7411 | 514295.3618 | 11089.1743 | 679460.7579 | 15283.2015 | 932585.8111 | 20271.8212 | 1230585.1946 | 24310.0326 | 1467219.4555 | 28513.1691 | 1708936.7923 | 33343.2688 | 1980150.7301 | 39920.3021 | 2339808.4438 | [5 empty] | 133373.075 | 7920602.9205 | 256618.5217 | 15380431.1308
1.5 | 3.0845 | 82 | 1 | 1 | 85.6 | 6.9 | 70 | 759.5656 | 774.9119 |  | 768.2099 | 42849.8683 | 1143.9856 | 63779.1534 | 1911.8337 | 106481.7069 | 2990.6444 | 166313.8727 | 4641.7441 | 257434.5799 | 6304.4696 | 348682.7377 | 8356.055 | 460661.8197 | 11547.5645 | 632275.9215 | 15358.2386 | 834313.9887 | 18463.971 | 994747.6384 | 21713.1812 | 1158627.5195 | 25468.1877 | 1342505.5503 | 30607.3023 | 1586346.8243 | [5 empty] | 101872.7509 | 5370022.2011 | 195418.6306 | 10427647.6758
2.2 | 4.7511 | 77 | 1 | 1 | 86.8 | 8.5 | 63 | 360.2711 | 444.1028 |  | 530.0736 | 24347.7968 | 788.6787 | 36211.9937 | 1315.8225 | 60365.5836 | 2053.4284 | 94081.1091 | 3175.0363 | 145115.8543 | 4297.52 | 195913.988 | 5675.4112 | 257934.8111 | 7790.6602 | 351714.5183 | 10292.672 | 461030.0777 | 12297.7804 | 546270.5166 | 14369.233 | 632136.647 | 16730.3232 | 727009.6717 | 19922.4356 | 851185.8212 | [5 empty] | 66921.293 | 2908038.6867 | 129323.0972 | 5689229.8232
3 | 6.1095 | 81 | 1 | 1 | 87.5 | 7.9 | 62 | 296.6582 | 375.4171 |  | 392.4762 | 20599.7646 | 584.3579 | 30634.2611 | 976.2529 | 51056.5023 | 1526.4083 | 79548.3045 | 2367.321 | 122638.6154 | 3213.0947 | 165492.261 | 4255.5851 | 217775.3765 | 5872.9898 | 296678.9596 | 7800.4746 | 388524.5904 | 9366.0358 | 459955.8051 | 10999.6947 | 531768.2422 | 12882.2983 | 610939.6139 | 15452.2201 | 714375.785 | [5 empty] | 51529.1932 | 2443758.4555 | 98997.2521 | 4785914.18
5.5 | 10.5831 | 84 | 1 | 1 | 89.3 | 7 | 55 | 171.456 | 260.3527 |  | 218.7403 | 14545.0798 | 325.8518 | 21613.7475 | 544.9329 | 35968.6625 | 853.2427 | 55921.2309 | 1326.3366 | 85914.4652 | 1803.9678 | 115563.4237 | 2394.5443 | 151552.0318 | 3318.2398 | 205131.0807 | 4425.473 | 266884.9712 | 5334.1667 | 314029.8807 | 6289.8911 | 360763.3242 | 7400.8791 | 411493.4909 | 8929.5749 | 476943.2502 | [5 empty] | 29603.5164 | 1645973.9637 | 56609.0198 | 3246869.9179
7.5 | 13.7795 | 87 | 1 | 1 | 90.3 | 7.8 | 55 | 118.1772 | 179.4499 |  | 162.4008 | 10025.2966 | 242.0523 | 14897.4245 | 405.2101 | 24791.6487 | 635.3961 | 38544.0941 | 990.0249 | 59217.1378 | 1349.4517 | 79652.887 | 1795.3252 | 104458.2834 | 2498.5444 | 141388.0124 | 3346.7188 | 183952.3075 | 4050.3897 | 216447.2615 | 4796.7105 | 248658.6099 | 5672.413 | 283624.7273 | 6887.9923 | 328736.4253 | [5 empty] | 22689.6518 | 1134498.909 | 43170.3945 | 2237927.4891
15 | 28.7617 | 82 | 1 | 1 | 91.8 | 8.1 | 50 | 49.5644 | 85.8481 | [5 empty] | 205.0308 | 12129.6526 | 320.7256 | 18829.66 | 497.7945 | 28857.5747 | 676.1102 | 38727.3671 | 896.1283 | 50663.4851 | 1238.3953 | 68258.4027 | 1647.0634 | 88393.1006 | 1980.1315 | 103555.4394 | 2328.5865 | 118430.5435 | 2731.2846 | 134395.0272 | 3282.4186 | 154808.7917 | [5 empty] | 10925.1385 |  | 20957.2784
25 | 44.732 | 86 | 1 | 1 | 93.8 | 7.6 | 40 | 27.1724 | 62.2597 | [9 empty] | 307.8367 | 22233.9218 | 419.2906 | 29702.027 | 557.3977 | 38665.9472 | 774.6017 | 51610.8845 | 1036.0266 | 66205.9531 | 1252.1155 | 76881.5743 | 1480.6462 | 87126.9142 | 1747.9385 | 97859.3439 | 2117.8457 | 111335.9745 | [5 empty] | 6991.7539 |  | 13325.8162
37 | 69.4328 | 82 | 1 | 1 | 93.8 | 7.4 | 40 | 17.9789 | 41.1948 | [13 empty] | 371.2102 | 25583.7505 | 512.9901 | 34148.9111 | 682.2759 | 43805.8993 | 820.2452 | 50869.5418 | 964.5885 | 57648.484 | 1131.4012 | 64749.7145 | 1359.7018 | 73666.6759 | [5 empty] | 4525.605 | 258998.8582 | 8681.2962 | 518836.356
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
Note : | SF and MF is using for running voltage drop.
Note : | For each cross section, the first cell shows the Max. length due to normal running, and the next cell shows Max. length due to Starting
The minimum number is Bold.

## LV Motor_1C_AG (hidden)
CABLE SIZE SELECTION TABLE MOTOR FEEDER
LV Motor 1C AG (Outdoor)
|  | System Nominal Voltage |  |  | 0.4 | (kV) |  |  | A/G | Standard |  |  | IEC |  |  | Derating factor |  |  |  | 0.533
|  | Number of Phase |  |  | 3 | Ph |  |  | U/G | Unit System |  |  | Metric |  |  | Min Cable Size |  |  |  | 240
|  | System Frequency |  |  | 50 | (Hz) |  |  |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  |  | 400
|  | Voltage Drop @Running |  |  | 5 | (%) |  |  |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  |  | A/G
|  | Voltage Drop @Starting |  |  | 15 | (%) |  |  |  | Insulation Type |  |  | XLPE/AWA/PVC |  |  | Base Temperature (A/G) |  |  |  | 48
|  | Wiring System |  |  | 3ph-3W |  |  |  |  | Number of Cores |  |  | 1C |  |  | Base Temperature (U/G) |  |  |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size | [6 empty] | Run |  |  | 1 |  | 1 |  | 1 |  | 2 |  | 2 |  | 2 |  | 3 |  | 3 |  |  |  | 2 | 3
[7 empty] | Size (mm2) |  |  | 240 |  | 300 |  | 400 |  | 240 |  | 300 |  | 400 |  | 240 |  | 300 |  |  |  | 185 | 150
Nominal Ampacity (A) | [9 empty] | 607 |  | 703 |  | 823 |  | 1214 |  | 1406 |  | 1646 |  | 1821 |  | 2109 |  |  |  | #N/A | #N/A
Resistance (ohm/km) | [9 empty] | 0.0981 |  | 0.0792 |  | 0.0632 |  | 0.04905 |  | 0.0396 |  | 0.0316 |  | 0.0327 |  | 0.0264 |  |  |  | #N/A | #N/A
Reactance (ohm/km) | [9 empty] | 0.097 |  | 0.095 |  | 0.093 |  | 0.0485 |  | 0.0475 |  | 0.0465 |  | 0.032333 |  | 0.031667 |  |  |  | #N/A | #N/A
Derated Ampacity (A) (=Nominal Ampacity x Total Derating Factor x Run) | [9 empty] | 323.531 |  | 374.699 |  | 438.659 |  | 647.062 |  | 749.398 |  | 877.318 |  | 970.593 |  | 1124.097 |  | 0 | 0 | #N/A | #N/A
Output | Full Load |  | SF | MF | Eff. (%) | Locked Rotor |  | RL | XL | Maximum Cable Run (m)
kW | A | PF (%) |  |  |  | % | PF (%)
1.85 | 4.3897 | 79 | 1 | 1 | 77 | 500 | 70 | 7.3654 | 7.5142 | 19204.7857 | 13460.5984 | 21773.1802 | 15053.9894 | 24596.1836 | 16739.3836 | 38409.5715 | 26921.1969 | 43546.3604 | 30107.9789 | 49192.3673 | 33478.7671 | 57614.3572 | 40381.7953 | 65319.5406 | 45161.9683
15 | 29.6422 | 83 | 1 | 1 | 88 | 700 | 50 | 0.5565 | 0.96388 | 2874.3306 | 1467.9401 | 3281.1246 | 1608.0003 | 3733.8652 | 1750.759 | 5748.6612 | 2935.8801 | 6562.2492 | 3216.0007 | 7467.7303 | 3501.518 | 8622.9917 | 4403.8202 | 9843.3737 | 4824.001
55 | 99.7934 | 86 | 1 | 1 | 92.5 | 700 | 40 | 0.13224 | 0.303 | 864.3746 | 449.9711 | 992.445 | 488.2063 | 1136.5272 | 526.5091 | 1728.7492 | 899.9422 | 1984.8899 | 976.4127 | 2273.0544 | 1053.0183 | 2593.1238 | 1349.9132 | 2977.3349 | 1464.619
132 | 202.5144 | 96 | 1 | 1 | 98 | 735 | 35 | 0.054303 | 0.14534 | 469.9197 | 215.2794 | 555.5595 | 232.466 | 657.5581 | 249.5335 | 939.8395 | 430.5588 | 1111.119 | 464.932 | 1315.1163 | 499.0671 | 1409.7592 | 645.8382 | 1666.6785 | 697.398
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
Note : | SF and MF is using for running voltage drop.
Note : | For each cross section, the first cell shows the Max. length due to normal running, and the next cell shows Max. length due to Starting
The minimum number is Bold.
01
01

## LV Motor_1C_UG (hidden)
CABLE SIZE SELECTION TABLE MOTOR FEEDER
LV Motor 1C UG (Outdoor)
|  | System Nominal Voltage |  |  | 0.4 | (kV) |  |  | A/G | Standard |  |  | IEC |  |  | Derating factor |  |  |  | 0.533
|  | Number of Phase |  |  | 3 | Ph |  |  | U/G | Unit System |  |  | Metric |  |  | Min Cable Size |  |  |  | 240
|  | System Frequency |  |  | 50 | (Hz) |  |  |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  |  | 400
|  | Voltage Drop @Running |  |  | 5 | (%) |  |  |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  |  | U/G
|  | Voltage Drop @Starting |  |  | 15 | (%) |  |  |  | Insulation Type |  |  | XLPE/AWA/PVC |  |  | Base Temperature (A/G) |  |  |  | 48
|  | Wiring System |  |  | 3ph-3W |  |  |  |  | Number of Cores |  |  | 1C |  |  | Base Temperature (U/G) |  |  |  | 30
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size | [6 empty] | Run |  |  | 1 |  | 1 |  | 1 |  | 2 |  | 2 |  | 2 |  | 3 |  | 3 |  |  |  | 2 | 3
[7 empty] | Size (mm2) |  |  | 240 |  | 300 |  | 400 |  | 240 |  | 300 |  | 400 |  | 240 |  | 300 |  |  |  | 185 | 150
Nominal Ampacity (A) | [9 empty] | 448 |  | 502 |  | 558 |  | 896 |  | 1004 |  | 1116 |  | 1344 |  | 1506 |  |  |  | #N/A | #N/A
Resistance (ohm/km) | [9 empty] | 0.0981 |  | 0.0792 |  | 0.0632 |  | 0.04905 |  | 0.0396 |  | 0.0316 |  | 0.0327 |  | 0.0264 |  |  |  | #N/A | #N/A
Reactance (ohm/km) | [9 empty] | 0.097 |  | 0.095 |  | 0.093 |  | 0.0485 |  | 0.0475 |  | 0.0465 |  | 0.032333 |  | 0.031667 |  |  |  | #N/A | #N/A
Derated Ampacity (A) (=Nominal Ampacity x Total Derating Factor x Run) | [9 empty] | 238.784 |  | 267.566 |  | 297.414 |  | 477.568 |  | 535.132 |  | 594.828 |  | 716.352 |  | 802.698 |  | 0 | 0 | #N/A | #N/A
Output | Full Load |  | SF | MF | Eff. (%) | Locked Rotor |  | RL | XL | Maximum Cable Run (m)
kW | A | PF (%) |  |  |  | % | PF (%)
1.85 | 4.3897 | 79 | 1 | 1 | 77 | 500 | 70 | 7.3654 | 7.5142 | 19204.7857 | 13460.5984 | 21773.1802 | 15053.9894 | 24596.1836 | 16739.3836 | 38409.5715 | 26921.1969 | 43546.3604 | 30107.9789 | 49192.3673 | 33478.7671 | 57614.3572 | 40381.7953 | 65319.5406 | 45161.9683
15 | 29.6422 | 83 | 1 | 1 | 88 | 700 | 50 | 0.5565 | 0.96388 | 2874.3306 | 1467.9401 | 3281.1246 | 1608.0003 | 3733.8652 | 1750.759 | 5748.6612 | 2935.8801 | 6562.2492 | 3216.0007 | 7467.7303 | 3501.518 | 8622.9917 | 4403.8202 | 9843.3737 | 4824.001
55 | 99.7934 | 86 | 1 | 1 | 92.5 | 700 | 40 | 0.13224 | 0.303 | 864.3746 | 449.9711 | 992.445 | 488.2063 | 1136.5272 | 526.5091 | 1728.7492 | 899.9422 | 1984.8899 | 976.4127 | 2273.0544 | 1053.0183 | 2593.1238 | 1349.9132 | 2977.3349 | 1464.619
132 | 202.5144 | 96 | 1 | 1 | 98 | 735 | 35 | 0.054303 | 0.14534 | 469.9197 | 215.2794 | 555.5595 | 232.466 | 657.5581 | 249.5335 | 939.8395 | 430.5588 | 1111.119 | 464.932 | 1315.1163 | 499.0671 | 1409.7592 | 645.8382 | 1666.6785 | 697.398
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
[8 empty] | #DIV/0! | #DIV/0!
Note : | SF and MF is using for running voltage drop.
Note : | For each cross section, the first cell shows the Max. length due to normal running, and the next cell shows Max. length due to Starting
The minimum number is Bold.
01
01

## LV Feeder-3C-AG
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder 3C AG
|  |  |  | System Nominal Voltage |  |  | 0.4 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.61
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W/4W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 50
[10 empty] | Number of Cores |  |  | 3C |  |  | Base Temperature (U/G) |  |  | 35 | [11 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 240
Nominal Ampacity (A) | [5 empty] | 32 | 42 | 54 | 75 | 100 | 127 | 158 | 192 | 246 | 298 | 346 | 399 | 456 | 538 | 798 | 1076 | [8 empty] | Page 108 of LV Abhar
Resistance (ohm/km) | [5 empty] | 9.45 | 5.88 | 3.93 | 2.33 | 1.47 | 0.927 | 0.669 | 0.494 | 0.343 | 0.247 | 0.197 | 0.16 | 0.129 | 0.0996 | 0.08 | 0.0498 | [8 empty] | Page 15 of LV Cable Abhar
Reactance (ohm/km) | [5 empty] | 0.095 | 0.09 | 0.087 | 0.083 | 0.081 | 0.081 | 0.079 | 0.075 | 0.075 | 0.072 | 0.072 | 0.072 | 0.072 | 0.071 | 0.036 | 0.0355
Derated Ampacity (A) | [5 empty] | 19.52 | 25.62 | 32.94 | 45.75 | 61 | 77.47 | 96.38 | 117.12 | 150.06 | 181.78 | 211.06 | 243.39 | 278.16 | 328.18 | 486.78 | 656.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
0.6 |  | 1.0825 | 80 | 100 | 2.5 | 280.0753 | 448.3677 | 667.4593 | 1114.7107 | 1742.0654 | 2699.7385 | 3661.7462 | 4846.282 | 6679.1901 | 8859.3577 | 10624.17 | 12461.0592 | 14571.949 | 17446.2981 | 24922.1184 | 34892.5962
1.2 |  | 2.1651 | 80 | 100 | 2.5 | 140.0376 | 224.1838 | 333.7296 | 557.3553 | 871.0327 | 1349.8692 | 1830.8731 | 2423.141 | 3339.5951 | 4429.6788 | 5312.085 | 6230.5296 | 7285.9745 | 8723.1491 | 12461.0592 | 17446.2981
3 |  | 5.4127 | 80 | 100 | 2.5 | 56.0151 | 89.6735 | 133.4919 | 222.9421 | 348.4131 | 539.9477 | 732.3492 | 969.2564 | 1335.838 | 1771.8715 | 2124.834 | 2492.2118 | 2914.3898 | 3489.2596 | 4984.4237 | 6978.5192
5 |  | 9.0211 | 80 | 100 | 2.5 | 33.609 | 53.8041 | 80.0951 | 133.7653 | 209.0479 | 323.9686 | 439.4095 | 581.5538 | 801.5028 | 1063.1229 | 1274.9004 | 1495.3271 | 1748.6339 | 2093.5558 | 2990.6542 | 4187.1115
7.5 |  | 13.5316 | 80 | 100 | 2.5 | 22.406 | 35.8694 | 53.3967 | 89.1769 | 139.3652 | 215.9791 | 292.9397 | 387.7026 | 534.3352 | 708.7486 | 849.9336 | 996.8847 | 1165.7559 | 1395.7038 | 1993.7695 | 2791.4077
10 |  | 18.0422 | 80 | 100 | 2.5 | 16.8045 | 26.9021 | 40.0476 | 66.8826 | 104.5239 | 161.9843 | 219.7048 | 290.7769 | 400.7514 | 531.5615 | 637.4502 | 747.6636 | 874.3169 | 1046.7779 | 1495.3271 | 2093.5558
10.5 |  | 18.9443 | 80 | 100 | 2.5 | 16.0043 | 25.621 | 38.1405 | 63.6978 | 99.5466 | 154.2708 | 209.2426 | 276.9304 | 381.668 | 506.249 | 607.0954 | 712.0605 | 832.6828 | 996.9313 | 1424.1211 | 1993.8626
12 |  | 21.6506 | 80 | 100 | 2.5 |  | 22.4184 | 33.373 | 55.7355 | 87.1033 | 134.9869 | 183.0873 | 242.3141 | 333.9595 | 442.9679 | 531.2085 | 623.053 | 728.5974 | 872.3149 | 1246.1059 | 1744.6298
20 |  | 36.0844 | 80 | 100 | 2.5 |  |  |  | 33.4413 | 52.262 | 80.9922 | 109.8524 | 145.3885 | 200.3757 | 265.7807 | 318.7251 | 373.8318 | 437.1585 | 523.3889 | 747.6636 | 1046.7779
37 |  | 66.7561 | 80 | 100 | 2.5 | [5 empty] | 43.7795 | 59.3797 | 78.5884 | 108.3112 | 143.6653 | 172.2838 | 202.0712 | 236.3019 | 282.9129 | 404.1425 | 565.8259
52.5 |  | 94.7215 | 80 | 100 | 2.5 | [6 empty] | 41.8485 | 55.3861 | 76.3336 | 101.2498 | 121.4191 | 142.4121 | 166.5366 | 199.3863 | 284.8242 | 398.7725
120 |  | 216.5064 | 80 | 100 | 2.5 | [11 empty] | 62.3053 | 72.8597 | 87.2315 | 124.6106 | 174.463
150 |  | 270.6329 | 80 | 100 | 95 | [12 empty] | 58.2878 | 69.7852 | 99.6885 | 139.5704
179 |  | 322.9553 | 80 | 100 | 2.5 | [13 empty] | 58.4792 | 83.5378 | 116.9584
240 |  | 433.0127 | 80 | 100 | 2.5 | [14 empty] | 62.3053 | 87.2315

## LV Feeder-3C-AG (indoor) (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder-3C-AG (indoor)
|  |  |  | System Nominal Voltage |  |  | 0.4 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.56
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 2 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W/4W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 48
[10 empty] | Number of Cores |  |  | 3C |  |  | Base Temperature (U/G) |  |  | 30 | [5 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 4
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 120 | 150 | 185 | 240 | 150
Nominal Ampacity (A) | [5 empty] | 32 | 42 | 54 | 75 | 100 | 127 | 158 | 192 | 246 | 298 | 346 | 399 | 456 | 538 | 692 | 798 | 912 | 1076 | 1596
Resistance (ohm/km) | [5 empty] | 9.45 | 5.88 | 3.93 | 2.33 | 1.47 | 0.927 | 0.669 | 0.493 | 0.342 | 0.247 | 0.197 | 0.16 | 0.1264 | 0.0961 | 0.0985 | 0.08 | 0.0632 | 0.04805 | 0.04
Reactance (ohm/km) | [5 empty] | 0.095 | 0.097 | 0.094 | 0.09 | 0.088 | 0.089 | 0.086 | 0.083 | 0.082 | 0.079 | 0.079 | 0.08 | 0.072 | 0.071 | 0.0395 | 0.04 | 0.036 | 0.0355 | 0.02
Derated Ampacity (A) | [5 empty] | 17.92 | 23.52 | 30.24 | 42 | 56 | 71.12 | 88.48 | 107.52 | 137.76 | 166.88 | 193.76 | 223.44 | 255.36 | 301.28 | 387.52 | 446.88 | 510.72 | 602.56 | 893.76
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
0.5 |  | 0.84904 | 85 | 100 | 2.5 | 676.0493 | 1085.276 | 1621.6538 | 2728.1846 | 4308.2284 | 6788.9679 | 9354.3118 | 12607.1842 | 17953.7954 | 24526.6005 | 30340.2119 | 36756.7568 | 46008.1191 | 58915.904 | 60680.4239 | 73513.5135 | 92016.2382 | 117831.8081 | 147027.027
0.75 |  | 1.2736 | 85 | 100 | 2.5 | 450.6996 | 723.5173 | 1081.1026 | 1818.7897 | 2872.1523 | 4525.9786 | 6236.2078 | 8404.7895 | 11969.1969 | 16351.067 | 20226.808 | 24504.5045 | 30672.0794 | 39277.2694 | 40453.6159 | 49009.009 | 61344.1588 | 78554.5387 | 98018.018
1.5 |  | 2.5471 | 85 | 100 | 2.5 | 225.3498 | 361.7587 | 540.5513 | 909.3949 | 1436.0761 | 2262.9893 | 3118.1039 | 4202.3947 | 5984.5985 | 8175.5335 | 10113.404 | 12252.2523 | 15336.0397 | 19638.6347 | 20226.808 | 24504.5045 | 30672.0794 | 39277.2694 | 49009.009
2 |  | 3.3962 | 85 | 100 | 2.5 | 169.0123 | 271.319 | 405.4135 | 682.0461 | 1077.0571 | 1697.242 | 2338.5779 | 3151.7961 | 4488.4488 | 6131.6501 | 7585.053 | 9189.1892 | 11502.0298 | 14728.976 | 15170.106 | 18378.3784 | 23004.0595 | 29457.952 | 36756.7568
3.5 |  | 5.9433 | 85 | 100 | 2.5 | 96.5785 | 155.0394 | 231.6648 | 389.7407 | 615.4612 | 969.8526 | 1336.3303 | 1801.0263 | 2564.8279 | 3503.8001 | 4334.316 | 5250.9653 | 6572.5884 | 8416.5577 | 8668.632 | 10501.9305 | 13145.1769 | 16833.1154 | 21003.861
4 |  | 6.7924 | 85 | 100 | 2.5 | 84.5062 | 135.6595 | 202.7067 | 341.0231 | 538.5285 | 848.621 | 1169.289 | 1575.898 | 2244.2244 | 3065.8251 | 3792.5265 | 4594.5946 | 5751.0149 | 7364.488 | 7585.053 | 9189.1892 | 11502.0298 | 14728.976 | 18378.3784
5 |  | 8.4904 | 85 | 100 | 2.5 | 67.6049 | 108.5276 | 162.1654 | 272.8185 | 430.8228 | 678.8968 | 935.4312 | 1260.7184 | 1795.3795 | 2452.6601 | 3034.0212 | 3675.6757 | 4600.8119 | 5891.5904 | 6068.0424 | 7351.3514 | 9201.6238 | 11783.1808 | 14702.7027
6 |  | 10.1885 | 85 | 100 | 2.5 | 56.3374 | 90.4397 | 135.1378 | 227.3487 | 359.019 | 565.7473 | 779.526 | 1050.5987 | 1496.1496 | 2043.8834 | 2528.351 | 3063.0631 | 3834.0099 | 4909.6587 | 5056.702 | 6126.1261 | 7668.0198 | 9819.3173 | 12252.2523
7 |  | 11.8866 | 85 | 100 | 2.5 | 48.2892 | 77.5197 | 115.8324 | 194.8703 | 307.7306 | 484.9263 | 668.1651 | 900.5132 | 1282.414 | 1751.9 | 2167.158 | 2625.4826 | 3286.2942 | 4208.2789 | 4334.316 | 5250.9653 | 6572.5884 | 8416.5577 | 10501.9305
8 |  | 13.5847 | 85 | 100 | 2.5 | 42.2531 | 67.8297 | 101.3534 | 170.5115 | 269.2643 | 424.3105 | 584.6445 | 787.949 | 1122.1122 | 1532.9125 | 1896.2632 | 2297.2973 | 2875.5074 | 3682.244 | 3792.5265 | 4594.5946 | 5751.0149 | 7364.488 | 9189.1892
9 |  | 15.2828 | 85 | 100 | 2.5 | 37.5583 | 60.2931 | 90.0919 | 151.5658 | 239.346 | 377.1649 | 519.684 | 700.3991 | 997.4331 | 1362.5889 | 1685.5673 | 2042.042 | 2556.0066 | 3273.1058 | 3371.1347 | 4084.0841 | 5112.0132 | 6546.2116 | 8168.1682
10 |  | 16.9809 | 85 | 100 | 2.5 | 33.8025 | 54.2638 | 81.0827 | 136.4092 | 215.4114 | 339.4484 | 467.7156 | 630.3592 | 897.6898 | 1226.33 | 1517.0106 | 1837.8378 | 2300.406 | 2945.7952 | 3034.0212 | 3675.6757 | 4600.8119 | 5891.5904 | 7351.3514
11 |  | 18.679 | 85 | 100 | 2.5 |  | 49.3307 | 73.7115 | 124.0084 | 195.8286 | 308.5895 | 425.196 | 573.0538 | 816.0816 | 1114.8455 | 1379.1005 | 1670.7617 | 2091.2781 | 2677.9956 | 2758.2011 | 3341.5233 | 4182.5563 | 5355.9913 | 6683.0467
12 |  | 20.3771 | 85 | 100 | 2.5 |  | 45.2198 | 67.5689 | 113.6744 | 179.5095 | 282.8737 | 389.763 | 525.2993 | 748.0748 | 1021.9417 | 1264.1755 | 1531.5315 | 1917.005 | 2454.8293 | 2528.351 | 3063.0631 | 3834.0099 | 4909.6587 | 6126.1261
13 |  | 22.0752 | 85 | 100 | 2.5 |  | 41.7414 | 62.3713 | 104.9302 | 165.7011 | 261.1142 | 359.7812 | 484.8917 | 690.5306 | 943.3308 | 1166.9312 | 1413.7214 | 1769.543 | 2265.9963 | 2333.8625 | 2827.4428 | 3539.0861 | 4531.9926 | 5654.8857
14 |  | 23.7732 | 85 | 100 | 2.5 |  |  | 57.9162 | 97.4352 | 153.8653 | 242.4631 | 334.0826 | 450.2566 | 641.207 | 875.95 | 1083.579 | 1312.7413 | 1643.1471 | 2104.1394 | 2167.158 | 2625.4826 | 3286.2942 | 4208.2789 | 5250.9653
15 |  | 25.4713 | 85 | 100 | 2.5 |  |  | 54.0551 | 90.9395 | 143.6076 | 226.2989 | 311.8104 | 420.2395 | 598.4598 | 817.5534 | 1011.3404 | 1225.2252 | 1533.604 | 1963.8635 | 2022.6808 | 2450.4505 | 3067.2079 | 3927.7269 | 4900.9009
16 |  | 27.1694 | 85 | 100 | 2.5 |  |  | 50.6767 | 85.2558 | 134.6321 | 212.1552 | 292.3222 | 393.9745 | 561.0561 | 766.4563 | 948.1316 | 1148.6486 | 1437.7537 | 1841.122 | 1896.2632 | 2297.2973 | 2875.5074 | 3682.244 | 4594.5946
17 |  | 28.8675 | 85 | 100 | 2.5 |  |  | 47.6957 | 80.2407 | 126.7126 | 199.6755 | 275.1268 | 370.7995 | 528.0528 | 721.3706 | 892.3592 | 1081.0811 | 1353.18 | 1732.8207 | 1784.7183 | 2162.1622 | 2706.3599 | 3465.6414 | 4324.3243
18 |  | 30.5656 | 85 | 100 | 2.5 |  |  |  | 75.7829 | 119.673 | 188.5824 | 259.842 | 350.1996 | 498.7165 | 681.2945 | 842.7837 | 1021.021 | 1278.0033 | 1636.5529 | 1685.5673 | 2042.042 | 2556.0066 | 3273.1058 | 4084.0841
19 |  | 32.2637 | 85 | 100 | 2.5 |  |  |  | 71.7943 | 113.3744 | 178.6571 | 246.1661 | 331.768 | 472.4683 | 645.4369 | 798.4266 | 967.2831 | 1210.74 | 1550.4185 | 1596.8533 | 1934.5661 | 2421.48 | 3100.8371 | 3869.1323
20 |  | 33.9618 | 85 | 100 | 2.5 |  |  |  | 68.2046 | 107.7057 | 169.7242 | 233.8578 | 315.1796 | 448.8449 | 613.165 | 758.5053 | 918.9189 | 1150.203 | 1472.8976 | 1517.0106 | 1837.8378 | 2300.406 | 2945.7952 | 3675.6757
30 |  | 50.9427 | 85 | 100 | 2.5 |  |  |  |  | 71.8038 | 113.1495 | 155.9052 | 210.1197 | 299.2299 | 408.7767 | 505.6702 | 612.6126 | 766.802 | 981.9317 | 1011.3404 | 1225.2252 | 1533.604 | 1963.8635 | 2450.4505
36 |  | 61.1312 | 85 | 100 | 2.5 | [5 empty] | 94.2912 | 129.921 | 175.0998 | 249.3583 | 340.6472 | 421.3918 | 510.5105 | 639.0017 | 818.2764 | 842.7837 | 1021.021 | 1278.0033 | 1636.5529 | 2042.042
37 |  | 62.8293 | 85 | 100 | 2.5 | [5 empty] | 91.7428 | 126.4096 | 170.3674 | 242.6189 | 331.4405 | 410.0029 | 496.7129 | 621.7313 | 796.1609 | 820.0057 | 993.4259 | 1243.4627 | 1592.3217 | 1986.8517
45 |  | 76.414 | 85 | 100 | 2.5 | [6 empty] | 103.9368 | 140.0798 | 199.4866 | 272.5178 | 337.1135 | 408.4084 | 511.2013 | 654.6212 | 674.2269 | 816.8168 | 1022.4026 | 1309.2423 | 1633.6336
50 |  | 84.9045 | 85 | 100 | 2.5 | [6 empty] | 93.5431 | 126.0718 | 179.538 | 245.266 | 303.4021 | 367.5676 | 460.0812 | 589.159 | 606.8042 | 735.1351 | 920.1624 | 1178.3181 | 1470.2703
75 |  | 127.3567 | 85 | 100 | 2.5 | [8 empty] | 119.692 | 163.5107 | 202.2681 | 245.045 | 306.7208 | 392.7727 | 404.5362 | 490.0901 | 613.4416 | 785.5454 | 980.1802
85 |  | 144.3376 | 85 | 100 | 2.5 | [9 empty] | 144.2741 | 178.4718 | 216.2162 | 270.636 | 346.5641 | 356.9437 | 432.4324 | 541.272 | 693.1283 | 864.8649
140 |  | 237.7325 | 85 | 100 | 2.5 | [12 empty] | 164.3147 | 210.4139 | 216.7158 | 262.5483 | 328.6294 | 420.8279 | 525.0965
150 |  | 254.7134 | 85 | 100 | 2.5 | [12 empty] | 153.3604 | 196.3863 | 202.2681 | 245.045 | 306.7208 | 392.7727 | 490.0901
160 |  | 271.6942 | 85 | 100 | 2.5 | [13 empty] | 184.1122 | 189.6263 | 229.7297 | 287.5507 | 368.2244 | 459.4595
200 |  | 339.6178 | 85 | 100 | 2.5 | [14 empty] | 151.7011 | 183.7838 | 230.0406 | 294.5795 | 367.5676
250 |  | 424.5223 | 85 | 100 | 2.5 | [15 empty] | 147.027 | 184.0325 | 235.6636 | 294.0541
300 |  | 509.4267 | 85 | 100 | 2.5 | [16 empty] | 153.3604 | 196.3863 | 245.045
ACB | 150 | 216.5064 | 85 | 100 | 300 | [15 empty] | 288.2883 | 360.848 | 462.0855 | 576.5766
ACB | 160 | 230.9401 | 85 | 100 | 300 | [15 empty] | 270.2703 | 338.295 | 433.2052 | 540.5405
ACB | 200 | 288.6751 | 85 | 100 | 300 | [15 empty] | 216.2162 | 270.636 | 346.5641 | 432.4324
ACB | 450 | 649.5191 | 85 | 100 | 300 | [18 empty] | 192.1922
ACB | 500 | 721.6878 | 85 | 100 | 300 | [18 empty] | 172.973
ACB | 600 | 866.0254 | 85 | 100 | 300 | [18 empty] | 144.1441

## LV Feeder-3C-AG indr (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder 3C AG (Indoor)
|  |  |  | System Nominal Voltage |  |  | 0.4 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.557
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 2 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W/4W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 55
[10 empty] | Number of Cores |  |  | 3C |  |  | Base Temperature (U/G) |  |  | 30 | [10 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 5 | 6
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240 | 150
Nominal Ampacity (A) | [5 empty] | 32 | 42 | 54 | 75 | 100 | 127 | 158 | 192 | 246 | 298 | 346 | 399 | 456 | 538 | 692 | 798 | 912 | 1076 | 1197 | 1368 | 1614 | 1824 | 2690 | 2394
Resistance (ohm/km) | [5 empty] | 9.45 | 5.88 | 3.93 | 2.33 | 1.47 | 0.927 | 0.669 | 0.493 | 0.342 | 0.247 | 0.197 | 0.16 | 0.1264 | 0.0961 | 0.0985 | 0.08 | 0.0632 | 0.04805 | 0.053333 | 0.042133 | 0.032033 | 0.0316 | 0.01922 | 0.026667
Reactance (ohm/km) | [5 empty] | 0.095 | 0.097 | 0.094 | 0.09 | 0.088 | 0.089 | 0.086 | 0.083 | 0.082 | 0.079 | 0.079 | 0.08 | 0.072 | 0.071 | 0.0395 | 0.04 | 0.036 | 0.0355 | 0.026667 | 0.024 | 0.023667 | 0.018 | 0.0142 | 0.013333
Derated Ampacity (A) | [5 empty] | 17.824 | 23.394 | 30.078 | 41.775 | 55.7 | 70.739 | 88.006 | 106.944 | 137.022 | 165.986 | 192.722 | 222.243 | 253.992 | 299.666 | 385.444 | 444.486 | 507.984 | 599.332 | 666.729 | 761.976 | 898.998 | 1015.968 | 1498.33 | 1333.458
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
0.5 |  | 0.84904 | 85 | 100 | 2.5 | 673.0554 | 1077.4202 | 1604.7114 | 2682.5642 | 4197.9945 | 6516.2682 | 8860.6086 | 11755.2243 | 16292.4895 | 21624.5583 | 26020.512 | 30537.331 | 37422.1752 | 45681.0534 | 52041.024 | 61074.662 | 74844.3505 | 91362.1068 | 91611.993 | 112266.5257 | 137043.1602 | 149688.701 | 228405.267 | 183223.986
0.7 |  | 1.1887 | 85 | 100 | 2.5 | 480.7538 | 769.5858 | 1146.2225 | 1916.1173 | 2998.5675 | 4654.4773 | 6329.0062 | 8396.5888 | 11637.4925 | 15446.1131 | 18586.08 | 21812.3793 | 26730.1252 | 32629.3239 | 37172.16 | 43624.7586 | 53460.2503 | 65258.6477 | 65437.1379 | 80190.3755 | 97887.9716 | 106920.5007 | 163146.6193 | 130874.2757
1.68 |  | 2.8528 | 85 | 100 | 2.5 | 200.3141 | 320.6608 | 477.5927 | 798.3822 | 1249.4031 | 1939.3655 | 2637.0859 | 3498.5787 | 4848.9552 | 6435.8804 | 7744.2 | 9088.4914 | 11137.5522 | 13595.5516 | 15488.4 | 18176.9827 | 22275.1043 | 27191.1032 | 27265.4741 | 33412.6565 | 40786.6548 | 44550.2086 | 67977.758 | 54530.9482
2 |  | 3.3962 | 85 | 100 | 2.5 | 168.2638 | 269.355 | 401.1779 | 670.6411 | 1049.4986 | 1629.067 | 2215.1522 | 2938.8061 | 4073.1224 | 5406.1396 | 6505.128 | 7634.3328 | 9355.5438 | 11420.2633 | 13010.256 | 15268.6655 | 18711.0876 | 22840.5267 | 22902.9983 | 28066.6314 | 34260.79 | 37422.1752 | 57101.3167 | 45805.9965
3 |  | 5.0943 | 85 | 100 | 2.5 | 112.1759 | 179.57 | 267.4519 | 447.094 | 699.6657 | 1086.0447 | 1476.7681 | 1959.2041 | 2715.4149 | 3604.093 | 4336.752 | 5089.5552 | 6237.0292 | 7613.5089 | 8673.504 | 10179.1103 | 12474.0584 | 15227.0178 | 15268.6655 | 18711.0876 | 22840.5267 | 24948.1168 | 38067.5445 | 30537.331
4.37 |  | 7.4206 | 85 | 100 | 2.5 | 77.0086 | 123.2746 | 183.6054 | 306.9295 | 480.3197 | 745.5684 | 1013.7996 | 1344.9913 | 1864.1292 | 2474.2058 | 2977.1753 | 3493.9738 | 4281.7134 | 5226.6651 | 5954.3506 | 6987.9476 | 8563.4268 | 10453.3303 | 10481.9214 | 12845.1402 | 15679.9954 | 17126.8537 | 26133.3257 | 20963.8428
5 |  | 8.4904 | 85 | 100 | 2.5 | 67.3055 | 107.742 | 160.4711 | 268.2564 | 419.7994 | 651.6268 | 886.0609 | 1175.5224 | 1629.2489 | 2162.4558 | 2602.0512 | 3053.7331 | 3742.2175 | 4568.1053 | 5204.1024 | 6107.4662 | 7484.435 | 9136.2107 | 9161.1993 | 11226.6526 | 13704.316 | 14968.8701 | 22840.5267 | 18322.3986
8.65 |  | 14.6885 | 85 | 100 | 2.5 | 38.9049 | 62.2786 | 92.7579 | 155.0615 | 242.6586 | 376.6629 | 512.1739 | 679.4927 | 941.7624 | 1249.9745 | 1504.0758 | 1765.1636 | 2163.1315 | 2640.5233 | 3008.1517 | 3530.3273 | 4326.263 | 5281.0466 | 5295.4909 | 6489.3946 | 7921.57 | 8652.5261 | 13202.6166 | 10590.9819
9 |  | 15.2828 | 85 | 100 | 2.5 | 37.392 | 59.8567 | 89.1506 | 149.0313 | 233.2219 | 362.0149 | 492.256 | 653.068 | 905.1383 | 1201.3643 | 1445.584 | 1696.5184 | 2079.0097 | 2537.8363 | 2891.168 | 3393.0368 | 4158.0195 | 5075.6726 | 5089.5552 | 6237.0292 | 7613.5089 | 8316.0389 | 12689.1815 | 10179.1103
10 |  | 16.9809 | 85 | 100 | 2.5 | 33.6528 | 53.871 | 80.2356 | 134.1282 | 209.8997 | 325.8134 | 443.0304 | 587.7612 | 814.6245 | 1081.2279 | 1301.0256 | 1526.8666 | 1871.1088 | 2284.0527 | 2602.0512 | 3053.7331 | 3742.2175 | 4568.1053 | 4580.5997 | 5613.3263 | 6852.158 | 7484.435 | 11420.2633 | 9161.1993
11 |  | 18.679 | 85 | 100 | 2.5 |  | 48.9736 | 72.9414 | 121.9347 | 190.8179 | 296.194 | 402.7549 | 534.3284 | 740.5677 | 982.9345 | 1182.7505 | 1388.0605 | 1701.008 | 2076.4115 | 2365.5011 | 2776.121 | 3402.0159 | 4152.823 | 4164.1815 | 5103.0239 | 6229.2346 | 6804.0319 | 10382.0576 | 8328.363
12 |  | 20.3771 | 85 | 100 | 2.5 |  | 44.8925 | 66.863 | 111.7735 | 174.9164 | 271.5112 | 369.192 | 489.801 | 678.8537 | 901.0233 | 1084.188 | 1272.3888 | 1559.2573 | 1903.3772 | 2168.376 | 2544.7776 | 3118.5146 | 3806.7544 | 3817.1664 | 4677.7719 | 5710.1317 | 6237.0292 | 9516.8861 | 7634.3328
14 |  | 23.7732 | 85 | 100 | 2.5 |  |  | 57.3111 | 95.8059 | 149.9284 | 232.7239 | 316.4503 | 419.8294 | 581.8746 | 772.3057 | 929.304 | 1090.619 | 1336.5063 | 1631.4662 | 1858.608 | 2181.2379 | 2673.0125 | 3262.9324 | 3271.8569 | 4009.5188 | 4894.3986 | 5346.025 | 8157.331 | 6543.7138
15 |  | 25.4713 | 85 | 100 | 2.5 |  |  | 53.4904 | 89.4188 | 139.9331 | 217.2089 | 295.3536 | 391.8408 | 543.083 | 720.8186 | 867.3504 | 1017.911 | 1247.4058 | 1522.7018 | 1734.7008 | 2035.8221 | 2494.8117 | 3045.4036 | 3053.7331 | 3742.2175 | 4568.1053 | 4989.6234 | 7613.5089 | 6107.4662
16 |  | 27.1694 | 85 | 100 | 2.5 |  |  | 50.1472 | 83.8301 | 131.1873 | 203.6334 | 276.894 | 367.3508 | 509.1403 | 675.7674 | 813.141 | 954.2916 | 1169.443 | 1427.5329 | 1626.282 | 1908.5832 | 2338.886 | 2855.0658 | 2862.8748 | 3508.3289 | 4282.5988 | 4677.7719 | 7137.6646 | 5725.7496
18 |  | 30.5656 | 85 | 100 | 2.5 |  |  |  | 74.5157 | 116.611 | 181.0074 | 246.128 | 326.534 | 452.5692 | 600.6822 | 722.792 | 848.2592 | 1039.5049 | 1268.9181 | 1445.584 | 1696.5184 | 2079.0097 | 2537.8363 | 2544.7776 | 3118.5146 | 3806.7544 | 4158.0195 | 6344.5907 | 5089.5552
20 |  | 33.9618 | 85 | 100 | 2.5 |  |  |  | 67.0641 | 104.9499 | 162.9067 | 221.5152 | 293.8806 | 407.3122 | 540.614 | 650.5128 | 763.4333 | 935.5544 | 1142.0263 | 1301.0256 | 1526.8666 | 1871.1088 | 2284.0527 | 2290.2998 | 2806.6631 | 3426.079 | 3742.2175 | 5710.1317 | 4580.5997
22 |  | 37.358 | 85 | 100 | 2.5 |  |  |  | 60.9674 | 95.409 | 148.097 | 201.3775 | 267.1642 | 370.2839 | 491.4672 | 591.3753 | 694.0303 | 850.504 | 1038.2058 | 1182.7505 | 1388.0605 | 1701.008 | 2076.4115 | 2082.0908 | 2551.5119 | 3114.6173 | 3402.0159 | 5191.0288 | 4164.1815
24 |  | 40.7541 | 85 | 100 | 2.5 |  |  |  | 55.8868 | 87.4582 | 135.7556 | 184.596 | 244.9005 | 339.4269 | 450.5116 | 542.094 | 636.1944 | 779.6287 | 951.6886 | 1084.188 | 1272.3888 | 1559.2573 | 1903.3772 | 1908.5832 | 2338.886 | 2855.0658 | 3118.5146 | 4758.4431 | 3817.1664
28 |  | 47.5465 | 85 | 100 | 2.5 |  |  |  |  | 74.9642 | 116.3619 | 158.2252 | 209.9147 | 290.9373 | 386.1528 | 464.652 | 545.3095 | 668.2531 | 815.7331 | 929.304 | 1090.619 | 1336.5063 | 1631.4662 | 1635.9284 | 2004.7594 | 2447.1993 | 2673.0125 | 4078.6655 | 3271.8569
30 |  | 50.9427 | 85 | 100 | 2.5 |  |  |  |  | 69.9666 | 108.6045 | 147.6768 | 195.9204 | 271.5415 | 360.4093 | 433.6752 | 508.9555 | 623.7029 | 761.3509 | 867.3504 | 1017.911 | 1247.4058 | 1522.7018 | 1526.8666 | 1871.1088 | 2284.0527 | 2494.8117 | 3806.7544 | 3053.7331
50.5 |  | 85.7535 | 85 | 100 | 2.5 | [6 empty] | 87.7288 | 116.3884 | 161.3118 | 214.1045 | 257.6288 | 302.3498 | 370.5166 | 452.2877 | 515.2577 | 604.6996 | 741.0332 | 904.5753 | 907.0494 | 1111.5498 | 1356.863 | 1482.0663 | 2261.4383 | 1814.0989
60 |  | 101.8853 | 85 | 100 | 2.5 | [7 empty] | 97.9602 | 135.7707 | 180.2047 | 216.8376 | 254.4778 | 311.8515 | 380.6754 | 433.6752 | 508.9555 | 623.7029 | 761.3509 | 763.4333 | 935.5544 | 1142.0263 | 1247.4058 | 1903.3772 | 1526.8666
70 |  | 118.8662 | 85 | 100 | 2.5 | [8 empty] | 116.3749 | 154.4611 | 185.8608 | 218.1238 | 267.3013 | 326.2932 | 371.7216 | 436.2476 | 534.6025 | 652.5865 | 654.3714 | 801.9038 | 978.8797 | 1069.205 | 1631.4662 | 1308.7428
75 |  | 127.3567 | 85 | 100 | 2.5 | [8 empty] | 108.6166 | 144.1637 | 173.4701 | 203.5822 | 249.4812 | 304.5404 | 346.9402 | 407.1644 | 498.9623 | 609.0807 | 610.7466 | 748.4435 | 913.6211 | 997.9247 | 1522.7018 | 1221.4932
100 |  | 169.8089 | 85 | 100 | 2.5 | [10 empty] | 130.1026 | 152.6867 | 187.1109 | 228.4053 | 260.2051 | 305.3733 | 374.2218 | 456.8105 | 458.06 | 561.3326 | 685.2158 | 748.4435 | 1142.0263 | 916.1199
101 |  | 171.507 | 85 | 100 | 2.5 | [10 empty] | 128.8144 | 151.1749 | 185.2583 | 226.1438 | 257.6288 | 302.3498 | 370.5166 | 452.2877 | 453.5247 | 555.7749 | 678.4315 | 741.0332 | 1130.7191 | 907.0494
150 |  | 254.7134 | 85 | 100 | 2.5 | [13 empty] | 152.2702 | 173.4701 | 203.5822 | 249.4812 | 304.5404 | 305.3733 | 374.2218 | 456.8105 | 498.9623 | 761.3509 | 610.7466
200 |  | 339.6178 | 85 | 100 | 2.5 | [14 empty] | 130.1026 | 152.6867 | 187.1109 | 228.4053 | 229.03 | 280.6663 | 342.6079 | 374.2218 | 571.0132 | 458.06
220 |  | 373.5796 | 85 | 100 | 2.5 | [14 empty] | 118.2751 | 138.8061 | 170.1008 | 207.6412 | 208.2091 | 255.1512 | 311.4617 | 340.2016 | 519.1029 | 416.4182
250 |  | 424.5223 | 85 | 100 | 2.5 | [15 empty] | 122.1493 | 149.6887 | 182.7242 | 183.224 | 224.5331 | 274.0863 | 299.3774 | 456.8105 | 366.448
253 |  | 429.6165 | 85 | 100 | 2.5 | [15 empty] | 120.7009 | 147.9137 | 180.5575 | 181.0514 | 221.8706 | 270.8363 | 295.8275 | 451.3938 | 362.1027
280 |  | 475.4649 | 85 | 100 | 2.5 | [16 empty] | 133.6506 | 163.1466 | 163.5928 | 200.4759 | 244.7199 | 267.3013 | 407.8665 | 327.1857
440 |  | 747.1592 | 85 | 100 | 240 | [19 empty] | 127.5756 | 155.7309 | 170.1008 | 259.5514 | 208.2091
ACB | 300 | 433.0127 | 85 | 100 | 400 | [17 empty] | 179.1414 | 179.6314 | 220.1304 | 268.7121 | 293.5073 | 447.8535 | 359.2627
ACB | 784 | 1131.6065 | 85 | 100 | 400 | [22 empty] | 171.3725 | 137.473

## LV Feeder-3C-UG
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder 3C UG
|  |  |  | System Nominal Voltage |  |  | 0.4 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.52
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | U/G
|  |  |  | Wiring System |  |  | 3ph-3W/4W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 50
[10 empty] | Number of Cores |  |  | 3C |  |  | Base Temperature (U/G) |  |  | 35 | [11 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 120 | 150 | 185 | 240 | 150 | 185
Nominal Ampacity (A) | [5 empty] | 30 | 39 | 49 | 65 | 84 | 107 | 129 | 153 | 188 | 226 | 257 | 287 | 324 | 375 | 514 | 574 | 648 | 750 | 861 | 972 |  |  |  |  | Installation type D2, page 46 of IEC60364
Resistance (ohm/km) | [5 empty] | 9.45 | 5.88 | 3.93 | 2.33 | 1.47 | 0.927 | 0.669 | 0.494 | 0.343 | 0.247 | 0.197 | 0.16 | 0.129 | 0.0996 | 0.0985 | 0.08 | 0.0645 | 0.0498 | 0.053333 | 0.043 |  |  |  |  | Page 15 of LV Cable Abhar
Reactance (ohm/km) | [5 empty] | 0.095 | 0.09 | 0.087 | 0.083 | 0.081 | 0.081 | 0.079 | 0.075 | 0.075 | 0.072 | 0.072 | 0.072 | 0.072 | 0.071 | 0.036 | 0.036 | 0.036 | 0.0355 | 0.024 | 0.024
Derated Ampacity (A) | [5 empty] | 15.6 | 20.28 | 25.48 | 33.8 | 43.68 | 55.64 | 67.08 | 79.56 | 97.76 | 117.52 | 133.64 | 149.24 | 168.48 | 195 | 267.28 | 298.48 | 336.96 | 390 | 447.72 | 505.44 | 0 | 0 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
0.6 |  | 1.0825 | 80 | 100 | 2.5 | 280.0753 | 448.3677 | 667.4593 | 1114.7107 | 1742.0654 | 2699.7385 | 3661.7462 | 4846.282 | 6679.1901 | 8859.3577 | 10624.17 | 12461.0592 | 14571.949 | 17446.2981 | 21248.34 | 24922.1184 | 29143.898 | 34892.5962 | 37383.1776 | 43715.847
1.2 |  | 2.1651 | 80 | 100 | 2.5 | 140.0376 | 224.1838 | 333.7296 | 557.3553 | 871.0327 | 1349.8692 | 1830.8731 | 2423.141 | 3339.5951 | 4429.6788 | 5312.085 | 6230.5296 | 7285.9745 | 8723.1491 | 10624.17 | 12461.0592 | 14571.949 | 17446.2981 | 18691.5888 | 21857.9235
3 |  | 5.4127 | 80 | 100 | 2.5 | 56.0151 | 89.6735 | 133.4919 | 222.9421 | 348.4131 | 539.9477 | 732.3492 | 969.2564 | 1335.838 | 1771.8715 | 2124.834 | 2492.2118 | 2914.3898 | 3489.2596 | 4249.668 | 4984.4237 | 5828.7796 | 6978.5192 | 7476.6355 | 8743.1694
5 |  | 9.0211 | 80 | 100 | 2.5 | 33.609 | 53.8041 | 80.0951 | 133.7653 | 209.0479 | 323.9686 | 439.4095 | 581.5538 | 801.5028 | 1063.1229 | 1274.9004 | 1495.3271 | 1748.6339 | 2093.5558 | 2549.8008 | 2990.6542 | 3497.2678 | 4187.1115 | 4485.9813 | 5245.9016
7.5 |  | 13.5316 | 80 | 100 | 2.5 | 22.406 | 35.8694 | 53.3967 | 89.1769 | 139.3652 | 215.9791 | 292.9397 | 387.7026 | 534.3352 | 708.7486 | 849.9336 | 996.8847 | 1165.7559 | 1395.7038 | 1699.8672 | 1993.7695 | 2331.5118 | 2791.4077 | 2990.6542 | 3497.2678
10 |  | 18.0422 | 80 | 100 | 2.5 |  | 26.9021 | 40.0476 | 66.8826 | 104.5239 | 161.9843 | 219.7048 | 290.7769 | 400.7514 | 531.5615 | 637.4502 | 747.6636 | 874.3169 | 1046.7779 | 1274.9004 | 1495.3271 | 1748.6339 | 2093.5558 | 2242.9907 | 2622.9508
10.5 |  | 18.9443 | 80 | 100 | 2.5 |  | 25.621 | 38.1405 | 63.6978 | 99.5466 | 154.2708 | 209.2426 | 276.9304 | 381.668 | 506.249 | 607.0954 | 712.0605 | 832.6828 | 996.9313 | 1214.1909 | 1424.1211 | 1665.3656 | 1993.8626 | 2136.1816 | 2498.0484
12 |  | 21.6506 | 80 | 100 | 2.5 |  |  | 33.373 | 55.7355 | 87.1033 | 134.9869 | 183.0873 | 242.3141 | 333.9595 | 442.9679 | 531.2085 | 623.053 | 728.5974 | 872.3149 | 1062.417 | 1246.1059 | 1457.1949 | 1744.6298 | 1869.1589 | 2185.7923
20 |  | 36.0844 | 80 | 100 | 2.5 |  |  |  |  | 52.262 | 80.9922 | 109.8524 | 145.3885 | 200.3757 | 265.7807 | 318.7251 | 373.8318 | 437.1585 | 523.3889 | 637.4502 | 747.6636 | 874.3169 | 1046.7779 | 1121.4953 | 1311.4754
37 |  | 66.7561 | 80 | 100 | 2.5 | [6 empty] | 59.3797 | 78.5884 | 108.3112 | 143.6653 | 172.2838 | 202.0712 | 236.3019 | 282.9129 | 344.5677 | 404.1425 | 472.6038 | 565.8259 | 606.2137 | 708.9056
52.5 |  | 94.7215 | 80 | 100 | 2.5 | [8 empty] | 76.3336 | 101.2498 | 121.4191 | 142.4121 | 166.5366 | 199.3863 | 242.8382 | 284.8242 | 333.0731 | 398.7725 | 427.2363 | 499.6097
120 |  | 216.5064 | 80 | 100 | 2.5 | [14 empty] | 106.2417 | 124.6106 | 145.7195 | 174.463 | 186.9159 | 218.5792
150 |  | 270.6329 | 80 | 100 | 95 | [15 empty] | 99.6885 | 116.5756 | 139.5704 | 149.5327 | 174.8634
179 |  | 322.9553 | 80 | 100 | 2.5 | [16 empty] | 97.689 | 116.9584 | 125.3067 | 146.5336
250 |  | 451.0549 | 80 | 100 | 2.5 | [19 empty] | 104.918

## LV Feeder-1C-AG
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder 1C AG
|  |  |  | System Nominal Voltage |  |  | 0.4 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.72
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 400
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W/4W |  |  | Insulation Type |  |  | XLPE/AWA/PVC |  |  | Base Temperature (A/G) |  |  | 50
[10 empty] | Number of Cores |  |  | 1C |  |  | Base Temperature (U/G) |  |  | 35 |  |  | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 4
[5 empty] | Size | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400
Nominal Ampacity (A) | [5 empty] | 607 | 703 | 823 | 1214 | 1406 | 1646 | 1821 | 2109 | 2469 | 2428 | 2812 | 3292 |  |  |  | Page 108 of LV Abhar
Resistance (ohm/km) | [5 empty] | 0.0981 | 0.0792 | 0.0632 | 0.04905 | 0.0396 | 0.0316 | 0.0327 | 0.0264 | 0.021067 | 0.024525 | 0.0198 | 0.0158 |  |  |  | Page 30 of LV Cable Abhar
Reactance (ohm/km) | [5 empty] | 0.183 | 0.178 | 0.171 | 0.0915 | 0.089 | 0.0855 | 0.061 | 0.059333 | 0.057 | 0.04575 | 0.0445 | 0.04275
Derated Ampacity (A) | [5 empty] | 437.04 | 506.16 | 592.56 | 874.08 | 1012.32 | 1185.12 | 1311.12 | 1518.48 | 1777.68 | 1748.16 | 2024.64 | 2370.24 | 0 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
| 1250 | 1804.2196 | 80 | 100 | 95 | [10 empty] | 30.0893 | 33.4291

## LV Feeder-1C-AG (indoor) (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder-1C-AG (indoor)
|  |  |  | System Nominal Voltage |  |  | 0.4 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.78
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 400
|  |  |  | Voltage Drop |  |  | 2 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W/4W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 45
[10 empty] | Number of Cores |  |  | 1C |  |  | Base Temperature (U/G) |  |  | 30 |  | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 5 | 5
[5 empty] | Size | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400 | 300 | 400 | 300 | 400
Nominal Ampacity (A) | [5 empty] | 607 | 703 | 823 | 1214 | 1406 | 1646 | 1821 | 2109 | 2469 | 2812 | 3292 | 3515 | 4115
Resistance (ohm/km) | [5 empty] | 0.0981 | 0.0792 | 0.0632 | 0.04905 | 0.0396 | 0.0316 | 0.0327 | 0.0264 | 0.021067 | 0.0198 | 0.0158 | 0.01584 | 0.01264
Reactance (ohm/km) | [5 empty] | 0.097 | 0.095 | 0.093 | 0.0485 | 0.0475 | 0.0465 | 0.032333 | 0.031667 | 0.031 | 0.02375 | 0.02325 | 0.019 | 0.0186
Derated Ampacity (A) | [5 empty] | 473.46 | 548.34 | 641.94 | 946.92 | 1096.68 | 1283.88 | 1420.38 | 1645.02 | 1925.82 | 2193.36 | 2567.76 | 2741.7 | 3209.7 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
150 |  | 254.7134 | 85 | 100 | 2.5 | 185.1568 | 222.304 | 267.9671 | 370.3136 | 444.6079 | 535.9342 | 555.4705 | 666.9119 | 803.9013 | 889.2158 | 1071.8684 | 1111.5198 | 1339.8355
160 |  | 271.6942 | 85 | 100 | 2.5 | 173.5845 | 208.41 | 251.2192 | 347.169 | 416.8199 | 502.4383 | 520.7536 | 625.2299 | 753.6575 | 833.6398 | 1004.8766 | 1042.0498 | 1256.0958
200 |  | 339.6178 | 85 | 100 | 2.5 | 138.8676 | 166.728 | 200.9753 | 277.7352 | 333.4559 | 401.9506 | 416.6028 | 500.1839 | 602.926 | 666.9119 | 803.9013 | 833.6398 | 1004.8766
250 |  | 424.5223 | 85 | 100 | 2.5 | 111.0941 | 133.3824 | 160.7803 | 222.1882 | 266.7647 | 321.5605 | 333.2823 | 400.1471 | 482.3408 | 533.5295 | 643.121 | 666.9119 | 803.9013
300 |  | 509.4267 | 85 | 100 | 2.5 |  | 111.152 | 133.9835 | 185.1568 | 222.304 | 267.9671 | 277.7352 | 333.4559 | 401.9506 | 444.6079 | 535.9342 | 555.7599 | 669.9177
ACB | 150 | 216.5064 | 85 | 100 | 300 |  | 261.5341 | 315.2554 | 435.6631 | 523.0681 | 630.5108 | 653.4947 | 784.6022 | 945.7662 | 1046.1362 | 1261.0216 | 1307.6703 | 1576.277
ACB | 160 | 230.9401 | 85 | 100 | 300 |  | 245.1882 | 295.5519 | 408.4342 | 490.3764 | 591.1039 | 612.6512 | 735.5645 | 886.6558 | 980.7527 | 1182.2078 | 1225.9409 | 1477.7597
ACB | 200 | 288.6751 | 85 | 100 | 300 |  | 196.1505 | 236.4416 | 326.7473 | 392.3011 | 472.8831 | 490.121 | 588.4516 | 709.3247 | 784.6022 | 945.7662 | 980.7527 | 1182.2078
ACB | 450 | 649.5191 | 85 | 100 | 300 |  |  |  | 145.221 | 174.356 | 210.1703 | 217.8316 | 261.5341 | 315.2554 | 348.7121 | 420.3405 | 435.8901 | 525.4257
ACB | 500 | 721.6878 | 85 | 100 | 300 |  |  |  | 130.6989 | 156.9204 | 189.1532 | 196.0484 | 235.3807 | 283.7299 | 313.8409 | 378.3065 | 392.3011 | 472.8831
ACB | 600 | 866.0254 | 85 | 100 | 300 |  |  |  | 108.9158 | 130.767 | 157.6277 | 163.3737 | 196.1505 | 236.4416 | 261.5341 | 315.2554 | 326.9176 | 394.0693

## LV Feeder-1C-AG indr (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder 1C AG (Indoor)
|  |  |  | System Nominal Voltage |  |  | 0.4 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.748
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 400
|  |  |  | Voltage Drop |  |  | 2 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W/4W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 55
[10 empty] | Number of Cores |  |  | 1C |  |  | Base Temperature (U/G) |  |  | 30 |  | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 5 | 5
[5 empty] | Size | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400 | 300 | 400 | 300 | 400
Nominal Ampacity (A) | [5 empty] | 634 | 736 | 868 | 1268 | 1472 | 1736 | 1902 | 2208 | 2604 | 2944 | 3472 | 3680 | 4340
Resistance (ohm/km) | [5 empty] | 0.0981 | 0.0792 | 0.0632 | 0.04905 | 0.0396 | 0.0316 | 0.0327 | 0.0264 | 0.021067 | 0.0198 | 0.0158 | 0.01584 | 0.01264
Reactance (ohm/km) | [5 empty] | 0.097 | 0.095 | 0.093 | 0.0485 | 0.0475 | 0.0465 | 0.032333 | 0.031667 | 0.031 | 0.02375 | 0.02325 | 0.019 | 0.0186
Derated Ampacity (A) | [5 empty] | 474.232 | 550.528 | 649.264 | 948.464 | 1101.056 | 1298.528 | 1422.696 | 1651.584 | 1947.792 | 2202.112 | 2597.056 | 2752.64 | 3246.32 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
200 |  | 339.6178 | 85 | 100 | 2.5 | 101.1281 | 115.8785 | 132.4106 | 202.2562 | 231.7569 | 264.8213 | 303.3842 | 347.6354 | 397.2319 | 463.5138 | 529.6425 | 579.3923 | 662.0531
220 |  | 373.5796 | 85 | 100 | 2.5 | 91.9346 | 105.344 | 120.3733 | 183.8692 | 210.6881 | 240.7466 | 275.8039 | 316.0321 | 361.1199 | 421.3762 | 481.4932 | 526.7202 | 601.8665
250 |  | 424.5223 | 85 | 100 | 2.5 | 80.9025 | 92.7028 | 105.9285 | 161.8049 | 185.4055 | 211.857 | 242.7074 | 278.1083 | 317.7855 | 370.8111 | 423.714 | 463.5138 | 529.6425
253 |  | 429.6165 | 85 | 100 | 2.5 | 79.9431 | 91.6035 | 104.6724 | 159.8863 | 183.207 | 209.3449 | 239.8294 | 274.8106 | 314.0173 | 366.4141 | 418.6897 | 458.0176 | 523.3622
280 |  | 475.4649 | 85 | 100 | 2.5 |  | 82.7703 | 94.579 | 144.4687 | 165.5406 | 189.158 | 216.703 | 248.311 | 283.7371 | 331.0813 | 378.3161 | 413.8516 | 472.8951
440 |  | 747.1592 | 85 | 100 | 240 |  |  |  | 91.9346 | 105.344 | 120.3733 | 137.9019 | 158.0161 | 180.5599 | 210.6881 | 240.7466 | 263.3601 | 300.9332
ACB | 300 | 433.0127 | 85 | 100 | 400 |  |  | 103.8515 | 158.6323 | 181.7701 | 207.7029 | 237.9484 | 272.6552 | 311.5544 | 363.5402 | 415.4059 | 454.4253 | 519.2574
ACB | 784 | 1131.6065 | 85 | 100 | 400 | [5 empty] | 79.4782 | 91.0517 | 104.3323 | 119.2173 | 139.1098 | 158.9563 | 173.8872 | 198.6954

## LV Feeder-1C-UG
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder 1C UG
|  |  |  | System Nominal Voltage |  |  | 0.4 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.52
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 400
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | U/G
|  |  |  | Wiring System |  |  | 3ph-3W/4W |  |  | Insulation Type |  |  | XLPE/AWA/PVC |  |  | Base Temperature (A/G) |  |  | 50
[10 empty] | Number of Cores |  |  | 1C |  |  | Base Temperature (U/G) |  |  | 35 |  |  | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 8 | 8 | 8
[5 empty] | Size | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400 | 240 | 300 | 400
Nominal Ampacity (A) | [5 empty] | 448 | 502 | 558 | 896 | 1004 | 1116 | 1344 | 1506 | 1674 | 3584 | 4016 | 4464 |  |  |  | Installation type D2, page 44 of IEC60364
Resistance (ohm/km) | [5 empty] | 0.0981 | 0.0792 | 0.0632 | 0.04905 | 0.0396 | 0.0316 | 0.0327 | 0.0264 | 0.021067 | 0.012263 | 0.0099 | 0.0079 |  |  |  | Page 30 of LV Cable Abhar
Reactance (ohm/km) | [5 empty] | 0.183 | 0.178 | 0.171 | 0.0915 | 0.089 | 0.0855 | 0.061 | 0.059333 | 0.057 | 0.022875 | 0.02225 | 0.021375
Derated Ampacity (A) | [5 empty] | 232.96 | 261.04 | 290.16 | 465.92 | 522.08 | 580.32 | 698.88 | 783.12 | 870.48 | 1863.68 | 2088.32 | 2321.28 | 0 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
150 |  | 270.6329 | 80 | 100 | 95 |  |  | 55.7152 | 90.6451 | 100.2978 | 111.4303 | 135.9677 | 150.4466 | 167.1455 | 362.5806 | 401.191 | 445.7213
179 |  | 322.9553 | 80 | 100 | 2.5 |  |  |  | 75.9596 | 84.0484 | 93.3774 | 113.9394 | 126.0726 | 140.066 | 303.8385 | 336.1936 | 373.5094
250 |  | 451.0549 | 80 | 100 | 2.5 |  |  |  | 54.3871 | 60.1787 | 66.8582 | 81.5806 | 90.268 | 100.2873 | 217.5483 | 240.7146 | 267.4328

## LV-Distribution Board-3C-UG (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV-Distribution Board-3C-UG
|  |  |  | System Nominal Voltage |  |  | 0.4 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.4
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 2 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | U/G
|  |  |  | Wiring System |  |  | 3ph-3W/4W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 55
[10 empty] | Number of Cores |  |  | 3.5-4C |  |  | Base Temperature (U/G) |  |  | 30 | [8 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 4 | 5
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240 | 185 | 240 | 240
Nominal Ampacity (A) | [5 empty] | 30 | 39 | 49 | 65 | 84 | 107 | 129 | 153 | 188 | 226 | 257 | 287 | 324 | 375 | 574 | 648 | 750 | 972 | 375 | 324 | 375 | 375
Resistance (ohm/km) | [5 empty] | 9.45 | 5.88 | 3.93 | 2.33 | 1.47 | 0.927 | 0.669 | 0.493 | 0.342 | 0.247 | 0.197 | 0.16 | 0.1264 | 0.0961 | 0.08 | 0.0632 | 0.04805 | 0.042133 | 0.0961 | 0.1264 | 0.0961 | 0.0961
Reactance (ohm/km) | [5 empty] | 0.095 | 0.097 | 0.094 | 0.09 | 0.088 | 0.089 | 0.086 | 0.083 | 0.082 | 0.079 | 0.079 | 0.08 | 0.072 | 0.071 | 0.04 | 0.036 | 0.0355 | 0.024 | 0.071 | 0.072 | 0.071 | 0.071
Derated Ampacity (A) | [5 empty] | 12 | 15.6 | 19.6 | 26 | 33.6 | 42.8 | 51.6 | 61.2 | 75.2 | 90.4 | 102.8 | 114.8 | 129.6 | 150 | 229.6 | 259.2 | 300 | 388.8 | 150 | 129.6 | 150 | 150
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
1 |  | 1.6981 | 85 | 100 | 2.5 | 338.0247 | 542.638 | 810.8269 | 1364.0923 | 2154.1142 | 3394.484 | 4677.1559 | 6303.5921 | 8976.8977 | 12263.3003 | 15170.106 | 18378.3784 | 23004.0595 | 29457.952 | 36756.7568 | 46008.1191 | 58915.904 | 69012.1786 | 88373.8561 | 92016.2382 | 117831.8081 | 147289.7601
1.5 |  | 2.5471 | 85 | 100 | 2.5 | 225.3498 | 361.7587 | 540.5513 | 909.3949 | 1436.0761 | 2262.9893 | 3118.1039 | 4202.3947 | 5984.5985 | 8175.5335 | 10113.404 | 12252.2523 | 15336.0397 | 19638.6347 | 24504.5045 | 30672.0794 | 39277.2694 | 46008.1191 | 58915.904 | 61344.1588 | 78554.5387 | 98193.1734
3 |  | 5.0943 | 85 | 100 | 2.5 | 112.6749 | 180.8793 | 270.2756 | 454.6974 | 718.0381 | 1131.4947 | 1559.052 | 2101.1974 | 2992.2992 | 4087.7668 | 5056.702 | 6126.1261 | 7668.0198 | 9819.3173 | 12252.2523 | 15336.0397 | 19638.6347 | 23004.0595 | 29457.952 | 30672.0794 | 39277.2694 | 49096.5867
9 |  | 15.2828 | 85 | 100 | 2.5 |  | 60.2931 | 90.0919 | 151.5658 | 239.346 | 377.1649 | 519.684 | 700.3991 | 997.4331 | 1362.5889 | 1685.5673 | 2042.042 | 2556.0066 | 3273.1058 | 4084.0841 | 5112.0132 | 6546.2116 | 7668.0198 | 9819.3173 | 10224.0265 | 13092.4231 | 16365.5289
10 |  | 16.9809 | 85 | 100 | 2.5 |  |  | 81.0827 | 136.4092 | 215.4114 | 339.4484 | 467.7156 | 630.3592 | 897.6898 | 1226.33 | 1517.0106 | 1837.8378 | 2300.406 | 2945.7952 | 3675.6757 | 4600.8119 | 5891.5904 | 6901.2179 | 8837.3856 | 9201.6238 | 11783.1808 | 14728.976
14 |  | 23.7732 | 85 | 100 | 2.5 |  |  |  | 97.4352 | 153.8653 | 242.4631 | 334.0826 | 450.2566 | 641.207 | 875.95 | 1083.579 | 1312.7413 | 1643.1471 | 2104.1394 | 2625.4826 | 3286.2942 | 4208.2789 | 4929.4413 | 6312.4183 | 6572.5884 | 8416.5577 | 10520.6972
18 |  | 30.5656 | 85 | 100 | 2.5 |  |  |  |  | 119.673 | 188.5824 | 259.842 | 350.1996 | 498.7165 | 681.2945 | 842.7837 | 1021.021 | 1278.0033 | 1636.5529 | 2042.042 | 2556.0066 | 3273.1058 | 3834.0099 | 4909.6587 | 5112.0132 | 6546.2116 | 8182.7645
28 |  | 47.5465 | 85 | 100 | 2.5 | [6 empty] | 167.0413 | 225.1283 | 320.6035 | 437.975 | 541.7895 | 656.3707 | 821.5736 | 1052.0697 | 1312.7413 | 1643.1471 | 2104.1394 | 2464.7207 | 3156.2091 | 3286.2942 | 4208.2789 | 5260.3486
30 |  | 50.9427 | 85 | 100 | 2.5 | [6 empty] | 155.9052 | 210.1197 | 299.2299 | 408.7767 | 505.6702 | 612.6126 | 766.802 | 981.9317 | 1225.2252 | 1533.604 | 1963.8635 | 2300.406 | 2945.7952 | 3067.2079 | 3927.7269 | 4909.6587
38 |  | 64.5274 | 85 | 100 | 2.5 | [8 empty] | 236.2341 | 322.7184 | 399.2133 | 483.6415 | 605.37 | 775.2093 | 967.2831 | 1210.74 | 1550.4185 | 1816.11 | 2325.6278 | 2421.48 | 3100.8371 | 3876.0463
40 |  | 67.9236 | 85 | 100 | 2.5 | [8 empty] | 224.4224 | 306.5825 | 379.2526 | 459.4595 | 575.1015 | 736.4488 | 918.9189 | 1150.203 | 1472.8976 | 1725.3045 | 2209.3464 | 2300.406 | 2945.7952 | 3682.244
45 |  | 76.414 | 85 | 100 | 2.5 | [9 empty] | 272.5178 | 337.1135 | 408.4084 | 511.2013 | 654.6212 | 816.8168 | 1022.4026 | 1309.2423 | 1533.604 | 1963.8635 | 2044.8053 | 2618.4846 | 3273.1058
50 |  | 84.9045 | 85 | 100 | 2.5 | [9 empty] | 245.266 | 303.4021 | 367.5676 | 460.0812 | 589.159 | 735.1351 | 920.1624 | 1178.3181 | 1380.2436 | 1767.4771 | 1840.3248 | 2356.6362 | 2945.7952
60 |  | 101.8853 | 85 | 100 | 2.5 | [10 empty] | 252.8351 | 306.3063 | 383.401 | 490.9659 | 612.6126 | 766.802 | 981.9317 | 1150.203 | 1472.8976 | 1533.604 | 1963.8635 | 2454.8293
80 |  | 135.8471 | 85 | 100 | 2.5 | [13 empty] | 368.2244 | 459.4595 | 575.1015 | 736.4488 | 862.6522 | 1104.6732 | 1150.203 | 1472.8976 | 1841.122
90 |  | 152.828 | 85 | 100 | 2.5 | [14 empty] | 408.4084 | 511.2013 | 654.6212 | 766.802 | 981.9317 | 1022.4026 | 1309.2423 | 1636.5529

## LV-LIGHTING BRANCH-3C-AG (PVC) (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV-LIGHTING BRANCH-3C-AG (PVC)
|  |  |  | System Nominal Voltage |  |  | 0.4 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.58
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 2.5 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W/4W |  |  | Insulation Type |  |  | PVC/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 45
[10 empty] | Number of Cores |  |  | 3C |  |  | Base Temperature (U/G) |  |  | 30 | [5 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 70
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 30 | 40 | 51 | 70 | 94 | 119 | 148 | 180 | 232 | 282 | 328 | 379 | 434 | 514 | 758 | 868 | 1028 | 533 | 634
Resistance (ohm/km) | [5 empty] | 9.45 | 5.88 | 3.93 | 2.33 | 1.47 | 0.927 | 0.669 | 0.493 | 0.342 | 0.247 | 0.197 | 0.16 | 0.1264 | 0.0961 | 0.08 | 0.0632 | 0.04805 | 0.1264 | 0.0961
Reactance (ohm/km) | [5 empty] | 0.095 | 0.097 | 0.094 | 0.09 | 0.088 | 0.089 | 0.086 | 0.083 | 0.082 | 0.079 | 0.079 | 0.08 | 0.072 | 0.071 | 0.04 | 0.036 | 0.0355 | 0.072 | 0.071
Derated Ampacity (A) | [5 empty] | 17.4 | 23.2 | 29.58 | 40.6 | 54.52 | 69.02 | 85.84 | 104.4 | 134.56 | 163.56 | 190.24 | 219.82 | 251.72 | 298.12 | 439.64 | 503.44 | 596.24 | 309.14 | 367.72
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
1 |  | 2.062 | 70 | 100 | 2.5 | 421.4646 | 675.4964 | 1007.4842 | 1688.7817 | 2653.0226 | 4144.4642 | 5666.8691 | 7567.5676 | 10606.0606 | 14242.116 | 17326.7327 | 20588.2353 | 25436.0465 | 31613.4131 | 41176.4706 | 50872.093 | 63226.8262 | 76308.1395 | 94840.2394
1.5 |  | 3.0929 | 70 | 100 | 2.5 | 280.9764 | 450.3309 | 671.6561 | 1125.8544 | 1768.6817 | 2762.9761 | 3777.9127 | 5045.045 | 7070.7071 | 9494.744 | 11551.1551 | 13725.4902 | 16957.3643 | 21075.6087 | 27450.9804 | 33914.7287 | 42151.2175 | 50872.093 | 63226.8262
3 |  | 6.1859 | 70 | 100 | 2.5 | 140.4882 | 225.1655 | 335.8281 | 562.9272 | 884.3409 | 1381.4881 | 1888.9564 | 2522.5225 | 3535.3535 | 4747.372 | 5775.5776 | 6862.7451 | 8478.6822 | 10537.8044 | 13725.4902 | 16957.3643 | 21075.6087 | 25436.0465 | 31613.4131
5 |  | 10.3098 | 70 | 100 | 2.5 | 84.2929 | 135.0993 | 201.4968 | 337.7563 | 530.6045 | 828.8928 | 1133.3738 | 1513.5135 | 2121.2121 | 2848.4232 | 3465.3465 | 4117.6471 | 5087.2093 | 6322.6826 | 8235.2941 | 10174.4186 | 12645.3652 | 15261.6279 | 18968.0479
5.5 |  | 11.3408 | 70 | 100 | 2.5 | 76.6299 | 122.8175 | 183.1789 | 307.0512 | 482.3677 | 753.5389 | 1030.3398 | 1375.9214 | 1928.3747 | 2589.4756 | 3150.315 | 3743.3155 | 4624.7357 | 5747.8933 | 7486.631 | 9249.4715 | 11495.7866 | 13874.2072 | 17243.6799
6.5 |  | 13.4028 | 70 | 100 | 2.5 | 64.8407 | 103.9225 | 154.9976 | 259.8126 | 408.1573 | 637.6099 | 871.826 | 1164.2412 | 1631.7016 | 2191.0948 | 2665.6512 | 3167.4208 | 3913.2379 | 4863.602 | 6334.8416 | 7826.4758 | 9727.204 | 11739.7138 | 14590.8061
10 |  | 20.6197 | 70 | 100 | 2.5 |  | 67.5496 | 100.7484 | 168.8782 | 265.3023 | 414.4464 | 566.6869 | 756.7568 | 1060.6061 | 1424.2116 | 1732.6733 | 2058.8235 | 2543.6047 | 3161.3413 | 4117.6471 | 5087.2093 | 6322.6826 | 7630.814 | 9484.0239
15 |  | 30.9295 | 70 | 100 | 2.5 |  |  |  | 112.5854 | 176.8682 | 276.2976 | 377.7913 | 504.5045 | 707.0707 | 949.4744 | 1155.1155 | 1372.549 | 1695.7364 | 2107.5609 | 2745.098 | 3391.4729 | 4215.1217 | 5087.2093 | 6322.6826
20 |  | 41.2393 | 70 | 100 | 2.5 |  |  |  |  | 132.6511 | 207.2232 | 283.3435 | 378.3784 | 530.303 | 712.1058 | 866.3366 | 1029.4118 | 1271.8023 | 1580.6707 | 2058.8235 | 2543.6047 | 3161.3413 | 3815.407 | 4742.012
25 |  | 51.5491 | 70 | 100 | 2.5 |  |  |  |  | 106.1209 | 165.7786 | 226.6748 | 302.7027 | 424.2424 | 569.6846 | 693.0693 | 823.5294 | 1017.4419 | 1264.5365 | 1647.0588 | 2034.8837 | 2529.073 | 3052.3256 | 3793.6096

## LV-SWGR to Panel-3C-AG (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV-SWGR to Panel-3C-AG
|  |  |  | System Nominal Voltage |  |  | 0.4 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.56
|  |  |  | Number of Phase |  |  | 3 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 3ph-3W/4W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 45
[10 empty] | Number of Cores |  |  | 3.5-4C |  |  | Base Temperature (U/G) |  |  | 30 | [8 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 4 | 4 | 5
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240 | 185 | 240 | 240
Nominal Ampacity (A) | [5 empty] | 32 | 42 | 54 | 75 | 100 | 127 | 158 | 192 | 246 | 298 | 346 | 399 | 456 | 538 | 798 | 912 | 1076 | 1368 | 375 | 324 | 375 | 375
Resistance (ohm/km) | [5 empty] | 9.45 | 5.88 | 3.93 | 2.33 | 1.47 | 0.927 | 0.669 | 0.493 | 0.342 | 0.247 | 0.197 | 0.16 | 0.1264 | 0.0961 | 0.08 | 0.0632 | 0.04805 | 0.042133 | 0.0961 | 0.1264 | 0.0961 | 0.0961
Reactance (ohm/km) | [5 empty] | 0.095 | 0.097 | 0.094 | 0.09 | 0.088 | 0.089 | 0.086 | 0.083 | 0.082 | 0.079 | 0.079 | 0.08 | 0.072 | 0.071 | 0.04 | 0.036 | 0.0355 | 0.024 | 0.071 | 0.072 | 0.071 | 0.071
Derated Ampacity (A) | [5 empty] | 17.92 | 23.52 | 30.24 | 42 | 56 | 71.12 | 88.48 | 107.52 | 137.76 | 166.88 | 193.76 | 223.44 | 255.36 | 301.28 | 446.88 | 510.72 | 602.56 | 766.08 | 210 | 181.44 | 210 | 210
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
1 |  | 1.9245 | 75 | 100 | 2.5 | 168.7467 | 270.6207 | 403.9044 | 677.9661 | 1067.141 | 1672.4739 | 2293.3588 | 3072.9834 | 4332.13 | 5853.6585 | 7164.1791 | 8571.4286 | 10638.2979 | 13359.3098 | 17142.8571 | 21276.5957 | 26718.6195 | 31914.8936 | 40077.9293 | 42553.1915 | 53437.2391 | 66796.5488
1.5 |  | 2.8868 | 75 | 100 | 2.5 | 112.4978 | 180.4138 | 269.2696 | 451.9774 | 711.4273 | 1114.9826 | 1528.9059 | 2048.6556 | 2888.0866 | 3902.439 | 4776.1194 | 5714.2857 | 7092.1986 | 8906.2065 | 11428.5714 | 14184.3972 | 17812.413 | 21276.5957 | 26718.6195 | 28368.7943 | 35624.8261 | 44531.0326
3 |  | 5.7735 | 75 | 100 | 2.5 | 56.2489 | 90.2069 | 134.6348 | 225.9887 | 355.7137 | 557.4913 | 764.4529 | 1024.3278 | 1444.0433 | 1951.2195 | 2388.0597 | 2857.1429 | 3546.0993 | 4453.1033 | 5714.2857 | 7092.1986 | 8906.2065 | 10638.2979 | 13359.3098 | 14184.3972 | 17812.413 | 22265.5163
5 |  | 9.6225 | 75 | 100 | 2.5 | 33.7493 | 54.1241 | 80.7809 | 135.5932 | 213.4282 | 334.4948 | 458.6718 | 614.5967 | 866.426 | 1170.7317 | 1432.8358 | 1714.2857 | 2127.6596 | 2671.862 | 3428.5714 | 4255.3191 | 5343.7239 | 6382.9787 | 8015.5859 | 8510.6383 | 10687.4478 | 13359.3098
5.5 |  | 10.5848 | 75 | 100 | 2.5 | 30.6812 | 49.2038 | 73.4372 | 123.2666 | 194.0256 | 304.0862 | 416.9743 | 558.7242 | 787.66 | 1064.3016 | 1302.578 | 1558.4416 | 1934.236 | 2428.9654 | 3116.8831 | 3868.472 | 4857.9308 | 5802.7079 | 7286.8962 | 7736.9439 | 9715.8617 | 12144.8271
6.5 |  | 12.5093 | 75 | 100 | 2.5 | 25.961 | 41.634 | 62.1391 | 104.3025 | 164.1755 | 257.3037 | 352.8244 | 472.7667 | 666.4815 | 900.5629 | 1102.1814 | 1318.6813 | 1636.6612 | 2055.2784 | 2637.3626 | 3273.3224 | 4110.5569 | 4909.9836 | 6165.8353 | 6546.6448 | 8221.1137 | 10276.3921
25 |  | 48.1125 | 75 | 100 | 2.5 |  |  |  |  | 42.6856 | 66.899 | 91.7344 | 122.9193 | 173.2852 | 234.1463 | 286.5672 | 342.8571 | 425.5319 | 534.3724 | 685.7143 | 851.0638 | 1068.7448 | 1276.5957 | 1603.1172 | 1702.1277 | 2137.4896 | 2671.862
27 |  | 51.9615 | 75 | 100 | 2.5 |  |  |  |  | 39.5237 | 61.9435 | 84.9392 | 113.8142 | 160.4493 | 216.8022 | 265.34 | 317.4603 | 394.011 | 494.7893 | 634.9206 | 788.0221 | 989.5785 | 1182.0331 | 1484.3678 | 1576.0441 | 1979.157 | 2473.9463
30 |  | 57.735 | 75 | 100 | 2.5 | [5 empty] | 55.7491 | 76.4453 | 102.4328 | 144.4043 | 195.122 | 238.806 | 285.7143 | 354.6099 | 445.3103 | 571.4286 | 709.2199 | 890.6207 | 1063.8298 | 1335.931 | 1418.4397 | 1781.2413 | 2226.5516
38 |  | 73.131 | 75 | 100 | 2.5 | [6 empty] | 60.3515 | 80.868 | 114.0034 | 154.0436 | 188.531 | 225.5639 | 279.9552 | 351.5608 | 451.1278 | 559.9104 | 703.1216 | 839.8656 | 1054.6824 | 1119.8208 | 1406.2431 | 1757.8039
40 |  | 76.98 | 75 | 100 | 2.5 | [6 empty] | 57.334 | 76.8246 | 108.3032 | 146.3415 | 179.1045 | 214.2857 | 265.9574 | 333.9827 | 428.5714 | 531.9149 | 667.9655 | 797.8723 | 1001.9482 | 1063.8298 | 1335.931 | 1669.9137
45 |  | 86.6025 | 75 | 100 | 2.5 | [6 empty] | 50.9635 | 68.2885 | 96.2696 | 130.0813 | 159.204 | 190.4762 | 236.4066 | 296.8736 | 380.9524 | 472.8132 | 593.7471 | 709.2199 | 890.6207 | 945.6265 | 1187.4942 | 1484.3678
50 |  | 96.225 | 75 | 100 | 2.5 | [7 empty] | 61.4597 | 86.6426 | 117.0732 | 143.2836 | 171.4286 | 212.766 | 267.1862 | 342.8571 | 425.5319 | 534.3724 | 638.2979 | 801.5586 | 851.0638 | 1068.7448 | 1335.931
60 |  | 115.4701 | 75 | 100 | 2.5 | [8 empty] | 72.2022 | 97.561 | 119.403 | 142.8571 | 177.305 | 222.6552 | 285.7143 | 354.6099 | 445.3103 | 531.9149 | 667.9655 | 709.2199 | 890.6207 | 1113.2758
80 |  | 153.9601 | 75 | 100 | 2.5 | [9 empty] | 73.1707 | 89.5522 | 107.1429 | 132.9787 | 166.9914 | 214.2857 | 265.9574 | 333.9827 | 398.9362 | 500.9741 | 531.9149 | 667.9655 | 834.9569
90 |  | 173.2051 | 75 | 100 | 2.5 | [10 empty] | 79.602 | 95.2381 | 118.2033 | 148.4368 | 190.4762 | 236.4066 | 296.8736 | 354.6099 | 445.3103 | 472.8132 | 593.7471 | 742.1839

## LV-XLPE-230VAC-AG
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV FEEDER XLPE 230VAC AG
|  |  |  | System Nominal Voltage |  |  | 0.23 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.61
|  |  |  | Number of Phase |  |  | 1 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 1ph-2W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 50
[10 empty] | Number of Cores |  |  | Multi C |  |  | Base Temperature (U/G) |  |  | 35 | [6 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 36 | 49 | 63 | 86 | 115 | 149 | 185 | 225 | 289 | 352 | 410 | 473 | 542 | 641 | [5 empty] | Page 108 of LV Abhar
Resistance (ohm/km) | [5 empty] | 9.45 | 5.88 | 3.93 | 2.33 | 1.47 | 0.927 | 0.668 | 0.494 | 0.342 | 0.247 | 0.196 | 0.16 | 0.1283 | 0.0987 | [5 empty] | Page 31 of LV Cable Abhar
Reactance (ohm/km) | [5 empty] | 0.095 | 0.09 | 0.087 | 0.083 | 0.081 | 0.081 | 0.079 | 0.075 | 0.075 | 0.072 | 0.072 | 0.072 | 0.072 | 0.071
Derated Ampacity (A) | [5 empty] | 21.96 | 29.89 | 38.43 | 52.46 | 70.15 | 90.89 | 112.85 | 137.25 | 176.29 | 214.72 | 250.1 | 288.53 | 330.62 | 391.01 | 0 | 0 | 0 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
0.5 |  | 2.7174 | 80 | 100 | 2.5 | 55.5599 | 88.9449 | 132.4072 | 221.1307 | 345.5822 | 535.5606 | 727.3977 | 961.3812 | 1328.3114 | 1757.4751 | 2116 | 2471.9626 | 2901.8102 | 3481.4084
1 |  | 5.4348 | 80 | 100 | 2.5 | 27.78 | 44.4725 | 66.2036 | 110.5654 | 172.7911 | 267.7803 | 363.6989 | 480.6906 | 664.1557 | 878.7375 | 1058 | 1235.9813 | 1450.9051 | 1740.7042
2 |  | 10.8696 | 80 | 100 | 2.5 | 13.89 | 22.2362 | 33.1018 | 55.2827 | 86.3956 | 133.8902 | 181.8494 | 240.3453 | 332.0778 | 439.3688 | 529 | 617.9907 | 725.4526 | 870.3521
3 |  | 16.3043 | 80 | 100 | 2.5 | 9.26 | 14.8242 | 22.0679 | 36.8551 | 57.597 | 89.2601 | 121.233 | 160.2302 | 221.3852 | 292.9125 | 352.6667 | 411.9938 | 483.635 | 580.2347
4 |  | 21.7391 | 80 | 100 | 2.5 | 6.945 | 11.1181 | 16.5509 | 27.6413 | 43.1978 | 66.9451 | 90.9247 | 120.1726 | 166.0389 | 219.6844 | 264.5 | 308.9953 | 362.7263 | 435.176
5 |  | 27.1739 | 80 | 100 | 2.5 |  | 8.8945 | 13.2407 | 22.1131 | 34.5582 | 53.5561 | 72.7398 | 96.1381 | 132.8311 | 175.7475 | 211.6 | 247.1963 | 290.181 | 348.1408

## LV FEEDER-PVC-230VAC-AG Outdr (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV FEEDER-PVC-230VAC-AG Outdr
|  |  |  | System Nominal Voltage |  |  | 0.23 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.39
|  |  |  | Number of Phase |  |  | 1 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 3 | (%) |  | Rated Voltage |  |  | 0.45/0.75kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 1ph-2W |  |  | Insulation Type |  |  | PVC/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 55
[10 empty] | Number of Cores |  |  | Multi C |  |  | Base Temperature (U/G) |  |  | 30 | [5 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 70
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 30 | 40 | 51 | 70 | 94 | 119 | 148 | 180 | 232 | 282 | 328 | 379 | 434 | 514 | 758 | 868 | 1028 | 1302 | 1542
Resistance (ohm/km) | [5 empty] | 9.45 | 5.51 | 3.686 | 2.19 | 1.386 | 0.87 | 0.627 | 0.463 | 0.321 | 0.231 | 0.183 | 0.148 | 0.119 | 0.0902 | 0.074 | 0.0595 | 0.0451 | 0.039667 | 0.030067
Reactance (ohm/km) | [5 empty] | 0.095 | 0.099 | 0.095 | 0.089 | 0.087 | 0.086 | 0.083 | 0.08 | 0.078 | 0.077 | 0.075 | 0.075 | 0.075 | 0.074 | 0.0375 | 0.0375 | 0.037 | 0.025 | 0.024667
Derated Ampacity (A) | [5 empty] | 11.7 | 15.6 | 19.89 | 27.3 | 36.66 | 46.41 | 57.72 | 70.2 | 90.48 | 109.98 | 127.92 | 147.81 | 169.26 | 200.46 | 295.62 | 338.52 | 400.92 | 507.78 | 601.38
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
0.1 |  | 0.54348 | 80 | 100 | 2.5 | 833.399 | 1420.9607 | 2111.917 | 3516.1183 | 5467.7003 | 8491.1717 | 11512.5136 | 15172.0841 | 20909.0909 | 27480.5195 | 33166.1442 | 38849.4492 | 45278.174 | 54461.2217 | 77698.8984 | 90556.3481 | 108922.4434 | 135834.5221 | 163383.6651
0.5 |  | 2.7174 | 80 | 100 | 2.5 | 166.6798 | 284.1921 | 422.3834 | 703.2237 | 1093.5401 | 1698.2343 | 2302.5027 | 3034.4168 | 4181.8182 | 5496.1039 | 6633.2288 | 7769.8898 | 9055.6348 | 10892.2443 | 15539.7797 | 18111.2696 | 21784.4887 | 27166.9044 | 32676.733
1 |  | 5.4348 | 80 | 100 | 2.5 | 83.3399 | 142.0961 | 211.1917 | 351.6118 | 546.77 | 849.1172 | 1151.2514 | 1517.2084 | 2090.9091 | 2748.0519 | 3316.6144 | 3884.9449 | 4527.8174 | 5446.1222 | 7769.8898 | 9055.6348 | 10892.2443 | 13583.4522 | 16338.3665
2 |  | 10.8696 | 80 | 100 | 2.5 | 41.6699 | 71.048 | 105.5958 | 175.8059 | 273.385 | 424.5586 | 575.6257 | 758.6042 | 1045.4545 | 1374.026 | 1658.3072 | 1942.4725 | 2263.9087 | 2723.0611 | 3884.9449 | 4527.8174 | 5446.1222 | 6791.7261 | 8169.1833
2.5 |  | 13.587 | 80 | 100 | 2.5 |  | 56.8384 | 84.4767 | 140.6447 | 218.708 | 339.6469 | 460.5005 | 606.8834 | 836.3636 | 1099.2208 | 1326.6458 | 1553.978 | 1811.127 | 2178.4489 | 3107.9559 | 3622.2539 | 4356.8977 | 5433.3809 | 6535.3466
4 |  | 21.7391 | 80 | 100 | 2.5 |  |  |  | 87.903 | 136.6925 | 212.2793 | 287.8128 | 379.3021 | 522.7273 | 687.013 | 829.1536 | 971.2362 | 1131.9544 | 1361.5305 | 1942.4725 | 2263.9087 | 2723.0611 | 3395.8631 | 4084.5916
5 |  | 27.1739 | 80 | 100 | 2.5 |  |  |  | 70.3224 | 109.354 | 169.8234 | 230.2503 | 303.4417 | 418.1818 | 549.6104 | 663.3229 | 776.989 | 905.5635 | 1089.2244 | 1553.978 | 1811.127 | 2178.4489 | 2716.6904 | 3267.6733

## LV FEEDER-XLPE-230VAC-AG indr (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV FEEDER XLPE 230VAC AG (Indoor)
|  |  |  | System Nominal Voltage |  |  | 0.23 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.557
|  |  |  | Number of Phase |  |  | 1 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 2 | (%) |  | Rated Voltage |  |  | 0.45/0.75kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 1ph-2W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 55
[10 empty] | Number of Cores |  |  | Multi C |  |  | Base Temperature (U/G) |  |  | 30 | [5 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 36 | 49 | 63 | 86 | 115 | 149 | 185 | 225 | 289 | 352 | 410 | 473 | 542 | 641 | 946 | 1084 | 1282 | 1626 | 1923
Resistance (ohm/km) | [5 empty] | 9.45 | 5.88 | 3.93 | 2.33 | 1.47 | 0.927 | 0.669 | 0.493 | 0.342 | 0.247 | 0.197 | 0.16 | 0.1264 | 0.0961 | 0.08 | 0.0632 | 0.04805 | 0.042133 | 0.032033
Reactance (ohm/km) | [5 empty] | 0.095 | 0.097 | 0.094 | 0.09 | 0.088 | 0.089 | 0.086 | 0.083 | 0.082 | 0.079 | 0.079 | 0.08 | 0.072 | 0.071 | 0.04 | 0.036 | 0.0355 | 0.024 | 0.023667
Derated Ampacity (A) | [5 empty] | 20.052 | 27.293 | 35.091 | 47.902 | 64.055 | 82.993 | 103.045 | 125.325 | 160.973 | 196.064 | 228.37 | 263.461 | 301.894 | 357.037 | 526.922 | 603.788 | 714.074 | 905.682 | 1071.111
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
0.5 |  | 2.7174 | 80 | 100 | 2.5 | 111.1199 | 177.733 | 264.4669 | 441.293 | 688.8021 | 1064.6541 | 1442.3995 | 1905.448 | 2622.057 | 3454.6939 | 4128.7805 | 4809.0909 | 5864.745 | 7084.0308 | 9618.1818 | 11729.49 | 14168.0616 | 17594.235 | 21252.0924
1 |  | 5.4348 | 80 | 100 | 2.5 | 55.5599 | 88.8665 | 132.2335 | 220.6465 | 344.401 | 532.327 | 721.1997 | 952.724 | 1311.0285 | 1727.3469 | 2064.3902 | 2404.5455 | 2932.3725 | 3542.0154 | 4809.0909 | 5864.745 | 7084.0308 | 8797.1175 | 10626.0462
2 |  | 10.8696 | 80 | 100 | 2.5 | 27.78 | 44.4332 | 66.1167 | 110.3233 | 172.2005 | 266.1635 | 360.5999 | 476.362 | 655.5143 | 863.6735 | 1032.1951 | 1202.2727 | 1466.1863 | 1771.0077 | 2404.5455 | 2932.3725 | 3542.0154 | 4398.5588 | 5313.0231
2.5 |  | 13.587 | 80 | 100 | 2.5 | 22.224 | 35.5466 | 52.8934 | 88.2586 | 137.7604 | 212.9308 | 288.4799 | 381.0896 | 524.4114 | 690.9388 | 825.7561 | 961.8182 | 1172.949 | 1416.8062 | 1923.6364 | 2345.898 | 2833.6123 | 3518.847 | 4250.4185
3 |  | 16.3043 | 80 | 100 | 2.5 | 18.52 | 29.6222 | 44.0778 | 73.5488 | 114.8003 | 177.4423 | 240.3999 | 317.5747 | 437.0095 | 575.7823 | 688.1301 | 801.5152 | 977.4575 | 1180.6718 | 1603.0303 | 1954.915 | 2361.3436 | 2932.3725 | 3542.0154
4 |  | 21.7391 | 80 | 100 | 2.5 |  | 22.2166 | 33.0584 | 55.1616 | 86.1003 | 133.0818 | 180.2999 | 238.181 | 327.7571 | 431.8367 | 516.0976 | 601.1364 | 733.0931 | 885.5039 | 1202.2727 | 1466.1863 | 1771.0077 | 2199.2794 | 2656.5116

## LV-PVC-230VAC-AG
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV FEEDER XLPE 230VAC AG
|  |  |  | System Nominal Voltage |  |  | 0.23 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.54
|  |  |  | Number of Phase |  |  | 1 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 1ph-2W |  |  | Insulation Type |  |  | CU/PVC/PVC |  |  | Base Temperature (A/G) |  |  | 50
[10 empty] | Number of Cores |  |  | Multi C |  |  | Base Temperature (U/G) |  |  | 35 | [6 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 30 | 40 | 51 | 70 | 94 | 119 | 148 | 180 | 232 | 282 | 328 | 379 | 434 | 514 | [5 empty] | Page 108 of LV Abhar
Resistance (ohm/km) | [5 empty] | 8.87 | 5.52 | 3.69 | 2.19 | 1.38 | 0.87 | 0.627 | 0.464 | 0.321 | 0.232 | 0.184 | 0.15 | 0.1205 | 0.0928 | [5 empty] | Page 6 of LV Cable Abhar
Reactance (ohm/km) | [5 empty] | 0.098 | 0.099 | 0.095 | 0.089 | 0.087 | 0.086 | 0.083 | 0.08 | 0.078 | 0.077 | 0.075 | 0.075 | 0.075 | 0.074
Derated Ampacity (A) | [5 empty] | 16.2 | 21.6 | 27.54 | 37.8 | 50.76 | 64.26 | 79.92 | 97.2 | 125.28 | 152.28 | 177.12 | 204.66 | 234.36 | 277.56 | 0 | 0 | 0 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
0.5 |  | 2.7174 | 80 | 100 | 2.5 | 59.1491 | 94.5614 | 140.6447 | 234.4079 | 366.0266 | 566.0781 | 767.5009 | 1009.542 | 1393.9394 | 1825.7118 | 2201.873 | 2564.8485 | 2992.9279 | 3567.0937
1 |  | 5.4348 | 80 | 100 | 2.5 | 29.5746 | 47.2807 | 70.3224 | 117.2039 | 183.0133 | 283.0391 | 383.7505 | 504.771 | 696.9697 | 912.8559 | 1100.9365 | 1282.4242 | 1496.4639 | 1783.5469
2 |  | 10.8696 | 80 | 100 | 2.5 | 14.7873 | 23.6403 | 35.1612 | 58.602 | 91.5067 | 141.5195 | 191.8752 | 252.3855 | 348.4848 | 456.428 | 550.4683 | 641.2121 | 748.232 | 891.7734
3 |  | 16.3043 | 80 | 100 | 2.5 |  | 15.7602 | 23.4408 | 39.068 | 61.0044 | 94.3464 | 127.9168 | 168.257 | 232.3232 | 304.2853 | 366.9788 | 427.4747 | 498.8213 | 594.5156
4 |  | 21.7391 | 80 | 100 | 2.5 |  |  | 17.5806 | 29.301 | 45.7533 | 70.7598 | 95.9376 | 126.1927 | 174.2424 | 228.214 | 275.2341 | 320.6061 | 374.116 | 445.8867
5 |  | 27.1739 | 80 | 100 | 2.5 |  |  | 14.0645 | 23.4408 | 36.6027 | 56.6078 | 76.7501 | 100.9542 | 139.3939 | 182.5712 | 220.1873 | 256.4848 | 299.2928 | 356.7094

## LV-XLPE-110V AC-AG
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder XLPE 110V AC 1PH AG
|  |  |  | System Nominal Voltage |  |  | 0.11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.61
|  |  |  | Number of Phase |  |  | 1 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 5 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 1ph-2W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 50
[10 empty] | Number of Cores |  |  | Multi C |  |  | Base Temperature (U/G) |  |  | 35 | [6 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 36 | 49 | 63 | 86 | 115 | 149 | 185 | 225 | 289 | 352 | 410 | 473 | 542 | 641 | [5 empty] | Page 108 of LV Abhar
Resistance (ohm/km) | [5 empty] | 9.45 | 5.88 | 3.93 | 2.33 | 1.47 | 0.927 | 0.668 | 0.494 | 0.342 | 0.247 | 0.196 | 0.16 | 0.1283 | 0.0987 | [5 empty] | Page 31 of LV Cable Abhar
Reactance (ohm/km) | [5 empty] | 0.095 | 0.09 | 0.087 | 0.083 | 0.081 | 0.081 | 0.079 | 0.075 | 0.075 | 0.072 | 0.072 | 0.072 | 0.072 | 0.071
Derated Ampacity (A) | [5 empty] | 21.96 | 29.89 | 38.43 | 52.46 | 70.15 | 90.89 | 112.85 | 137.25 | 176.29 | 214.72 | 250.1 | 288.53 | 330.62 | 391.01 | 0 | 0 | 0 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
1 |  | 11.3636 | 80 | 100 | 2.5 | 31.771 | 50.8617 | 75.7149 | 126.45 | 197.6155 | 306.2516 | 415.9505 | 549.7501 | 759.5731 | 1004.9834 | 1210 | 1413.5514 | 1659.3527 | 1990.7864
1.5 |  | 17.0455 | 80 | 100 | 2.5 | 21.1807 | 33.9078 | 50.4766 | 84.3 | 131.7437 | 204.1677 | 277.3003 | 366.5001 | 506.3821 | 669.9889 | 806.6667 | 942.3676 | 1106.2351 | 1327.191
2 |  | 22.7273 | 80 | 100 | 2.5 |  | 25.4309 | 37.8575 | 63.225 | 98.8078 | 153.1258 | 207.9752 | 274.8751 | 379.7866 | 502.4917 | 605 | 706.7757 | 829.6764 | 995.3932
2.5 |  | 28.4091 | 80 | 100 | 2.5 |  | 20.3447 | 30.286 | 50.58 | 79.0462 | 122.5006 | 166.3802 | 219.9 | 303.8293 | 401.9934 | 484 | 565.4206 | 663.7411 | 796.3146
3 |  | 34.0909 | 80 | 100 | 2.5 |  |  | 25.2383 | 42.15 | 65.8718 | 102.0839 | 138.6502 | 183.25 | 253.191 | 334.9945 | 403.3333 | 471.1838 | 553.1176 | 663.5955
4 |  | 45.4545 | 80 | 100 | 2.5 |  |  |  | 31.6125 | 49.4039 | 76.5629 | 103.9876 | 137.4375 | 189.8933 | 251.2458 | 302.5 | 353.3879 | 414.8382 | 497.6966

## LV FDR-XLPE-110V AC-1PH-AG Indr (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder XLPE 110V AC 1PH AG (Indoor)
|  |  |  | System Nominal Voltage |  |  | 0.11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.557
|  |  |  | Number of Phase |  |  | 1 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 3 | (%) |  | Rated Voltage |  |  | 0.45/0.75kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 1ph-2W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 45
[10 empty] | Number of Cores |  |  | Multi C |  |  | Base Temperature (U/G) |  |  | 30 | [5 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 36 | 49 | 63 | 86 | 115 | 149 | 185 | 225 | 289 | 352 | 410 | 473 | 542 | 641 | 946 | 1084 | 1282 | 1626 | 1923
Resistance (ohm/km) | [5 empty] | 9.45 | 5.88 | 3.93 | 2.33 | 1.47 | 0.927 | 0.669 | 0.493 | 0.342 | 0.247 | 0.197 | 0.16 | 0.1264 | 0.0961 | 0.08 | 0.0632 | 0.04805 | 0.042133 | 0.032033
Reactance (ohm/km) | [5 empty] | 0.095 | 0.097 | 0.094 | 0.09 | 0.088 | 0.089 | 0.086 | 0.083 | 0.082 | 0.079 | 0.079 | 0.08 | 0.072 | 0.071 | 0.04 | 0.036 | 0.0355 | 0.024 | 0.023667
Derated Ampacity (A) | [5 empty] | 20.052 | 27.293 | 35.091 | 47.902 | 64.055 | 82.993 | 103.045 | 125.325 | 160.973 | 196.064 | 228.37 | 263.461 | 301.894 | 357.037 | 526.922 | 603.788 | 714.074 | 905.682 | 1071.111
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
1 |  | 11.3636 | 80 | 100 | 2.5 | 19.0626 | 30.4901 | 45.3693 | 75.7039 | 118.1641 | 182.6415 | 247.4438 | 326.8798 | 449.8141 | 592.6531 | 708.2927 | 825 | 1006.0976 | 1215.2662 | 1650 | 2012.1951 | 2430.5323 | 3018.2927 | 3645.7985
1.5 |  | 17.0455 | 80 | 100 | 2.5 | 12.7084 | 20.3267 | 30.2462 | 50.4692 | 78.776 | 121.761 | 164.9625 | 217.9199 | 299.8761 | 395.102 | 472.1951 | 550 | 670.7317 | 810.1774 | 1100 | 1341.4634 | 1620.3549 | 2012.1951 | 2430.5323
2 |  | 22.7273 | 80 | 100 | 2.5 |  | 15.2451 | 22.6847 | 37.8519 | 59.082 | 91.3208 | 123.7219 | 163.4399 | 224.9071 | 296.3265 | 354.1463 | 412.5 | 503.0488 | 607.6331 | 825 | 1006.0976 | 1215.2662 | 1509.1463 | 1822.8992
2.5 |  | 28.4091 | 80 | 100 | 2.5 |  |  | 18.1477 | 30.2815 | 47.2656 | 73.0566 | 98.9775 | 130.7519 | 179.9257 | 237.0612 | 283.3171 | 330 | 402.439 | 486.1065 | 660 | 804.878 | 972.2129 | 1207.3171 | 1458.3194
3 |  | 34.0909 | 80 | 100 | 2.5 |  |  | 15.1231 | 25.2346 | 39.388 | 60.8805 | 82.4813 | 108.9599 | 149.938 | 197.551 | 236.0976 | 275 | 335.3659 | 405.0887 | 550 | 670.7317 | 810.1774 | 1006.0976 | 1215.2662
4 |  | 45.4545 | 80 | 100 | 2.5 |  |  |  | 18.926 | 29.541 | 45.6604 | 61.8609 | 81.7199 | 112.4535 | 148.1633 | 177.0732 | 206.25 | 251.5244 | 303.8165 | 412.5 | 503.0488 | 607.6331 | 754.5732 | 911.4496

## LV-PVC-110V AC-AG
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder PVC 110V AC 1PH AG
|  |  |  | System Nominal Voltage |  |  | 0.11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.54
|  |  |  | Number of Phase |  |  | 1 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 5 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 1ph-2W |  |  | Insulation Type |  |  | PVC/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 50
[10 empty] | Number of Cores |  |  | Multi C |  |  | Base Temperature (U/G) |  |  | 35 | [6 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 30 | 40 | 51 | 70 | 94 | 119 | 148 | 180 | 232 | 282 | 328 | 379 | 434 | 514 | [5 empty] | Page 106 of LV Abhar
Resistance (ohm/km) | [5 empty] | 8.87 | 5.52 | 3.69 | 2.19 | 1.38 | 0.87 | 0.627 | 0.464 | 0.321 | 0.232 | 0.184 | 0.15 | 0.1205 | 0.0928 | [5 empty] | Page 6 of LV Cable Abhar
Reactance (ohm/km) | [5 empty] | 0.098 | 0.099 | 0.095 | 0.089 | 0.087 | 0.086 | 0.083 | 0.08 | 0.078 | 0.077 | 0.075 | 0.075 | 0.075 | 0.074
Derated Ampacity (A) | [5 empty] | 16.2 | 21.6 | 27.54 | 37.8 | 50.76 | 64.26 | 79.92 | 97.2 | 125.28 | 152.28 | 177.12 | 204.66 | 234.36 | 277.56 | 0 | 0 | 0 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
1 |  | 11.3636 | 80 | 100 | 2.5 | 33.8234 | 54.0734 | 80.4254 | 134.0423 | 209.3063 | 323.7025 | 438.8828 | 577.2901 | 797.1014 | 1044.0035 | 1259.1051 | 1466.6667 | 1711.4569 | 2039.7842
1.5 |  | 17.0455 | 80 | 100 | 2.5 |  | 36.0489 | 53.6169 | 89.3615 | 139.5376 | 215.8017 | 292.5886 | 384.8601 | 531.401 | 696.0023 | 839.4034 | 977.7778 | 1140.9712 | 1359.8561
2 |  | 22.7273 | 80 | 100 | 2.5 |  |  | 40.2127 | 67.0212 | 104.6532 | 161.8513 | 219.4414 | 288.645 | 398.5507 | 522.0017 | 629.5525 | 733.3333 | 855.7284 | 1019.8921
2.5 |  | 28.4091 | 80 | 100 | 2.5 |  |  |  | 53.6169 | 83.7225 | 129.481 | 175.5531 | 230.916 | 318.8406 | 417.6014 | 503.642 | 586.6667 | 684.5827 | 815.9137
3 |  | 34.0909 | 80 | 100 | 2.5 |  |  |  | 44.6808 | 69.7688 | 107.9008 | 146.2943 | 192.43 | 265.7005 | 348.0012 | 419.7017 | 488.8889 | 570.4856 | 679.9281
4 |  | 45.4545 | 80 | 100 | 2.5 |  |  |  |  | 52.3266 | 80.9256 | 109.7207 | 144.3225 | 199.2754 | 261.0009 | 314.7763 | 366.6667 | 427.8642 | 509.9461
5 |  | 56.8182 | 80 | 100 | 2.5 | [5 empty] | 64.7405 | 87.7766 | 115.458 | 159.4203 | 208.8007 | 251.821 | 293.3333 | 342.2914 | 407.9568

## LV FDR-PVC-110V AC-1PH-AG Indr (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder PVC 110V AC 1PH AG (Indoor)
|  |  |  | System Nominal Voltage |  |  | 0.11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.506
|  |  |  | Number of Phase |  |  | 1 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 3 | (%) |  | Rated Voltage |  |  | 0.45/0.75kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 1ph-2W |  |  | Insulation Type |  |  | PVC/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 45
[10 empty] | Number of Cores |  |  | Multi C |  |  | Base Temperature (U/G) |  |  | 30 | [5 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 70
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 30 | 40 | 51 | 70 | 94 | 119 | 148 | 180 | 232 | 282 | 328 | 379 | 434 | 514 | 758 | 868 | 1028 | 1302 | 1542
Resistance (ohm/km) | [5 empty] | 9.45 | 5.51 | 3.686 | 2.19 | 1.386 | 0.87 | 0.627 | 0.463 | 0.321 | 0.231 | 0.183 | 0.148 | 0.119 | 0.0902 | 0.074 | 0.0595 | 0.0451 | 0.039667 | 0.030067
Reactance (ohm/km) | [5 empty] | 0.095 | 0.099 | 0.095 | 0.089 | 0.087 | 0.086 | 0.083 | 0.08 | 0.078 | 0.077 | 0.075 | 0.075 | 0.075 | 0.074 | 0.0375 | 0.0375 | 0.037 | 0.025 | 0.024667
Derated Ampacity (A) | [5 empty] | 15.18 | 20.24 | 25.806 | 35.42 | 47.564 | 60.214 | 74.888 | 91.08 | 117.392 | 142.692 | 165.968 | 191.774 | 219.604 | 260.084 | 383.548 | 439.208 | 520.168 | 658.812 | 780.252
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
1 |  | 11.3636 | 80 | 100 | 2.5 | 19.0626 | 32.5021 | 48.3066 | 80.4254 | 125.0646 | 194.2215 | 263.3297 | 347.0363 | 478.2609 | 628.5714 | 758.6207 | 888.6169 | 1035.6633 | 1245.7104 | 1777.2338 | 2071.3267 | 2491.4207 | 3106.99 | 3737.1311
1.5 |  | 17.0455 | 80 | 100 | 2.5 |  | 21.6681 | 32.2044 | 53.6169 | 83.3764 | 129.481 | 175.5531 | 231.3576 | 318.8406 | 419.0476 | 505.7471 | 592.4113 | 690.4422 | 830.4736 | 1184.8225 | 1380.8845 | 1660.9472 | 2071.3267 | 2491.4207
2 |  | 22.7273 | 80 | 100 | 2.5 |  |  | 24.1533 | 40.2127 | 62.5323 | 97.1108 | 131.6649 | 173.5182 | 239.1304 | 314.2857 | 379.3103 | 444.3084 | 517.8317 | 622.8552 | 888.6169 | 1035.6633 | 1245.7104 | 1553.495 | 1868.5655
2.5 |  | 28.4091 | 80 | 100 | 2.5 |  |  |  | 32.1702 | 50.0258 | 77.6886 | 105.3319 | 138.8145 | 191.3043 | 251.4286 | 303.4483 | 355.4468 | 414.2653 | 498.2841 | 710.8935 | 828.5307 | 996.5683 | 1242.796 | 1494.8524
3 |  | 34.0909 | 80 | 100 | 2.5 |  |  |  | 26.8085 | 41.6882 | 64.7405 | 87.7766 | 115.6788 | 159.4203 | 209.5238 | 252.8736 | 296.2056 | 345.2211 | 415.2368 | 592.4113 | 690.4422 | 830.4736 | 1035.6633 | 1245.7104
4 |  | 45.4545 | 80 | 100 | 2.5 |  |  |  |  | 31.2661 | 48.5554 | 65.8324 | 86.7591 | 119.5652 | 157.1429 | 189.6552 | 222.1542 | 258.9158 | 311.4276 | 444.3084 | 517.8317 | 622.8552 | 776.7475 | 934.2828
5 |  | 56.8182 | 80 | 100 | 2.5 | [5 empty] | 38.8443 | 52.6659 | 69.4073 | 95.6522 | 125.7143 | 151.7241 | 177.7234 | 207.1327 | 249.1421 | 355.4468 | 414.2653 | 498.2841 | 621.398 | 747.4262

## LV-XLPE-110V AC-UG
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder XLPE 110V AC 1PH UG
|  |  |  | System Nominal Voltage |  |  | 0.11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.61
|  |  |  | Number of Phase |  |  | 1 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 5 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 1ph-2W |  |  | Insulation Type |  |  | XLPE/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 50
[10 empty] | Number of Cores |  |  | Multi C |  |  | Base Temperature (U/G) |  |  | 35 | [6 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 36 | 49 | 63 | 86 | 115 | 149 | 185 | 225 | 289 | 352 | 410 | 473 | 542 | 641 | [5 empty] | Page 108 of LV Abhar
Resistance (ohm/km) | [5 empty] | 9.45 | 5.88 | 3.93 | 2.33 | 1.47 | 0.927 | 0.668 | 0.494 | 0.342 | 0.247 | 0.196 | 0.16 | 0.1283 | 0.0987 | [5 empty] | Page 31 of LV Cable Abhar
Reactance (ohm/km) | [5 empty] | 0.095 | 0.09 | 0.087 | 0.083 | 0.081 | 0.081 | 0.079 | 0.075 | 0.075 | 0.072 | 0.072 | 0.072 | 0.072 | 0.071
Derated Ampacity (A) | [5 empty] | 21.96 | 29.89 | 38.43 | 52.46 | 70.15 | 90.89 | 112.85 | 137.25 | 176.29 | 214.72 | 250.1 | 288.53 | 330.62 | 391.01 | 0 | 0 | 0 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
1 |  | 11.3636 | 80 | 100 | 2.5 | 31.771 | 50.8617 | 75.7149 | 126.45 | 197.6155 | 306.2516 | 415.9505 | 549.7501 | 759.5731 | 1004.9834 | 1210 | 1413.5514 | 1659.3527 | 1990.7864
1.5 |  | 17.0455 | 80 | 100 | 2.5 | 21.1807 | 33.9078 | 50.4766 | 84.3 | 131.7437 | 204.1677 | 277.3003 | 366.5001 | 506.3821 | 669.9889 | 806.6667 | 942.3676 | 1106.2351 | 1327.191
2 |  | 22.7273 | 80 | 100 | 2.5 |  | 25.4309 | 37.8575 | 63.225 | 98.8078 | 153.1258 | 207.9752 | 274.8751 | 379.7866 | 502.4917 | 605 | 706.7757 | 829.6764 | 995.3932
2.5 |  | 28.4091 | 80 | 100 | 2.5 |  | 20.3447 | 30.286 | 50.58 | 79.0462 | 122.5006 | 166.3802 | 219.9 | 303.8293 | 401.9934 | 484 | 565.4206 | 663.7411 | 796.3146
3 |  | 34.0909 | 80 | 100 | 2.5 |  |  | 25.2383 | 42.15 | 65.8718 | 102.0839 | 138.6502 | 183.25 | 253.191 | 334.9945 | 403.3333 | 471.1838 | 553.1176 | 663.5955
4 |  | 45.4545 | 80 | 100 | 2.5 |  |  |  | 31.6125 | 49.4039 | 76.5629 | 103.9876 | 137.4375 | 189.8933 | 251.2458 | 302.5 | 353.3879 | 414.8382 | 497.6966

## LV-PVC-110V AC-UG
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder PVC 110V AC 1PH UG
|  |  |  | System Nominal Voltage |  |  | 0.11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  | 0.54
|  |  |  | Number of Phase |  |  | 1 | Ph |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  | Refer to Min CSA
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  | 240
|  |  |  | Voltage Drop |  |  | 5 | (%) |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  | A/G
|  |  |  | Wiring System |  |  | 1ph-2W |  |  | Insulation Type |  |  | PVC/SWA/PVC |  |  | Base Temperature (A/G) |  |  | 50
[10 empty] | Number of Cores |  |  | Multi C |  |  | Base Temperature (U/G) |  |  | 35 | [6 empty] | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  |  |  |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[5 empty] | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240
Nominal Ampacity (A) | [5 empty] | 30 | 40 | 51 | 70 | 94 | 119 | 148 | 180 | 232 | 282 | 328 | 379 | 434 | 514 | [5 empty] | Page 106 of LV Abhar
Resistance (ohm/km) | [5 empty] | 8.87 | 5.52 | 3.69 | 2.19 | 1.38 | 0.87 | 0.627 | 0.464 | 0.321 | 0.232 | 0.184 | 0.15 | 0.1205 | 0.0928 | [5 empty] | Page 6 of LV Cable Abhar
Reactance (ohm/km) | [5 empty] | 0.098 | 0.099 | 0.095 | 0.089 | 0.087 | 0.086 | 0.083 | 0.08 | 0.078 | 0.077 | 0.075 | 0.075 | 0.075 | 0.074
Derated Ampacity (A) | [5 empty] | 16.2 | 21.6 | 27.54 | 37.8 | 50.76 | 64.26 | 79.92 | 97.2 | 125.28 | 152.28 | 177.12 | 204.66 | 234.36 | 277.56 | 0 | 0 | 0 | 0 | 0
Output |  | Full Load |  | Eff. (%) | Min. | Maximum Cable Run (m)
kW | kVA | A | PF (%) |  | CSA
1 |  | 11.3636 | 80 | 100 | 2.5 | 33.8234 | 54.0734 | 80.4254 | 134.0423 | 209.3063 | 323.7025 | 438.8828 | 577.2901 | 797.1014 | 1044.0035 | 1259.1051 | 1466.6667 | 1711.4569 | 2039.7842
1.5 |  | 17.0455 | 80 | 100 | 2.5 |  | 36.0489 | 53.6169 | 89.3615 | 139.5376 | 215.8017 | 292.5886 | 384.8601 | 531.401 | 696.0023 | 839.4034 | 977.7778 | 1140.9712 | 1359.8561
2 |  | 22.7273 | 80 | 100 | 2.5 |  |  | 40.2127 | 67.0212 | 104.6532 | 161.8513 | 219.4414 | 288.645 | 398.5507 | 522.0017 | 629.5525 | 733.3333 | 855.7284 | 1019.8921
2.5 |  | 28.4091 | 80 | 100 | 2.5 |  |  |  | 53.6169 | 83.7225 | 129.481 | 175.5531 | 230.916 | 318.8406 | 417.6014 | 503.642 | 586.6667 | 684.5827 | 815.9137
3 |  | 34.0909 | 80 | 100 | 2.5 |  |  |  | 44.6808 | 69.7688 | 107.9008 | 146.2943 | 192.43 | 265.7005 | 348.0012 | 419.7017 | 488.8889 | 570.4856 | 679.9281
4 |  | 45.4545 | 80 | 100 | 2.5 |  |  |  |  | 52.3266 | 80.9256 | 109.7207 | 144.3225 | 199.2754 | 261.0009 | 314.7763 | 366.6667 | 427.8642 | 509.9461
5 |  | 56.8182 | 80 | 100 | 2.5 | [5 empty] | 64.7405 | 87.7766 | 115.458 | 159.4203 | 208.8007 | 251.821 | 293.3333 | 342.2914 | 407.9568

## LV-110V DC-XLPE-AG
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder 110V DC XLPE AG
|  |  |  | System Nominal Voltage |  |  | 0.11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  |  | 0.61
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  |  | Refer-Min CSA
|  |  |  | Voltage Drop |  |  | 5 | (%) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  |  | 240
|  |  |  | Wiring System |  |  | DC-2W |  |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  |  | A/G
[10 empty] | Insulation Type |  |  | XLPE/PVC |  |  | Base Temperature (A/G) |  |  |  | 50
[10 empty] | Number of Cores |  |  | 2C |  |  | Base Temperature (U/G) |  |  |  | 35 |  |  | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240
Nominal Ampacity (A) |  |  | 36 | 49 | 63 | 86 | 115 | 149 | 185 | 225 | 289 | 352 | 410 | 473 | 542 | 641 | [5 empty] | Page 108 of LV Abhar
Resistance (ohm/km) |  |  | 9.45 | 5.88 | 3.93 | 2.33 | 1.47 | 0.927 | 0.668 | 0.494 | 0.342 | 0.247 | 0.196 | 0.16 | 0.1283 | 0.0987 | [5 empty] | Page 31 of LV Cable Abhar
Reactance (ohm/km)
Derated Ampacity (A) |  |  | 21.96 | 29.89 | 38.43 | 52.46 | 70.15 | 90.89 | 112.85 | 137.25 | 176.29 | 214.72 | 250.1 | 288.53 | 330.62 | 391.01 | 0 | 0 | 0 | 0 | 0
Output | Full Load | Min. | Maximum Cable Run (m)
kW | A | CSA
0.1 | 0.90909 | 2.5 | 320.1058 | 514.4558 | 769.7201 | 1298.2833 | 2057.8231 | 3263.2147 | 4528.4431 | 6123.4818 | 8845.0292 | 12246.9636 | 15433.6735 | 18906.25 | 23577.5526 | 30648.4296
0.5 | 4.5455 | 2.5 | 64.0212 | 102.8912 | 153.944 | 259.6567 | 411.5646 | 652.6429 | 905.6886 | 1224.6964 | 1769.0058 | 2449.3927 | 3086.7347 | 3781.25 | 4715.5105 | 6129.6859
1 | 9.0909 | 2.5 | 32.0106 | 51.4456 | 76.972 | 129.8283 | 205.7823 | 326.3215 | 452.8443 | 612.3482 | 884.5029 | 1224.6964 | 1543.3673 | 1890.625 | 2357.7553 | 3064.843
1.5 | 13.6364 | 2.5 | 21.3404 | 34.2971 | 51.3147 | 86.5522 | 137.1882 | 217.5476 | 301.8962 | 408.2321 | 589.6686 | 816.4642 | 1028.9116 | 1260.4167 | 1571.8368 | 2043.2286
2 | 18.1818 | 2.5 | 16.0053 | 25.7228 | 38.486 | 64.9142 | 102.8912 | 163.1607 | 226.4222 | 306.1741 | 442.2515 | 612.3482 | 771.6837 | 945.3125 | 1178.8776 | 1532.4215
0
0
0
0
0
0
0

## LV-FDR-110V DC-XLPE-AG Indoor (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder 110V DC XLPE AG (Indoor)
|  |  |  | System Nominal Voltage |  |  | 0.11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  |  | 0.557
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  |  | Refer-Min CSA
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  |  | 240
|  |  |  | Wiring System |  |  | DC-2W |  |  | Rated Voltage |  |  | 0.45/0.75kV |  |  | Installation |  |  |  | A/G
[10 empty] | Insulation Type |  |  | XLPE/PVC |  |  | Base Temperature (A/G) |  |  |  | 45
[10 empty] | Number of Cores |  |  | 2C |  |  | Base Temperature (U/G) |  |  |  | 30 |  | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3
|  | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240
Nominal Ampacity (A) |  |  | 36 | 49 | 63 | 86 | 115 | 149 | 185 | 225 | 289 | 352 | 410 | 473 | 542 | 641 | 946 | 1084 | 1282 | 1626 | 1923
Resistance (ohm/km) |  |  | 9.639 | 5.99 | 3.965 | 2.346 | 1.479 | 0.936 | 0.674 | 0.498 | 0.344 | 0.248 | 0.196 | 0.161 | 0.127 | 0.0971 | 0.0805 | 0.0635 | 0.04855 | 0.042333 | 0.032367
Reactance (ohm/km)
Derated Ampacity (A) |  |  | 20.052 | 27.293 | 35.091 | 47.902 | 64.055 | 82.993 | 103.045 | 125.325 | 160.973 | 196.064 | 228.37 | 263.461 | 301.894 | 357.037 | 526.922 | 603.788 | 714.074 | 905.682 | 1071.111
Output | Full Load | Min. | Maximum Cable Run (m)
kW | A | CSA
0.1 | 0.90909 | 2.5 | 62.7658 | 101.0017 | 152.5851 | 257.8858 | 409.0602 | 646.3675 | 897.6261 | 1214.8594 | 1758.7209 | 2439.5161 | 3086.7347 | 3757.764 | 4763.7795 | 6230.69 | 7515.528 | 9527.5591 | 12461.38 | 14291.3386 | 18692.07
0.5 | 4.5455 | 2.5 | 12.5532 | 20.2003 | 30.517 | 51.5772 | 81.812 | 129.2735 | 179.5252 | 242.9719 | 351.7442 | 487.9032 | 617.3469 | 751.5528 | 952.7559 | 1246.138 | 1503.1056 | 1905.5118 | 2492.276 | 2858.2677 | 3738.414
1 | 9.0909 | 2.5 | 6.2766 | 10.1002 | 15.2585 | 25.7886 | 40.906 | 64.6368 | 89.7626 | 121.4859 | 175.8721 | 243.9516 | 308.6735 | 375.7764 | 476.378 | 623.069 | 751.5528 | 952.7559 | 1246.138 | 1429.1339 | 1869.207
1.5 | 13.6364 | 2.5 | 4.1844 | 6.7334 | 10.1723 | 17.1924 | 27.2707 | 43.0912 | 59.8417 | 80.9906 | 117.2481 | 162.6344 | 205.7823 | 250.5176 | 317.5853 | 415.3793 | 501.0352 | 635.1706 | 830.7587 | 952.7559 | 1246.138
2 | 18.1818 | 2.5 | 3.1383 | 5.0501 | 7.6293 | 12.8943 | 20.453 | 32.3184 | 44.8813 | 60.743 | 87.936 | 121.9758 | 154.3367 | 187.8882 | 238.189 | 311.5345 | 375.7764 | 476.378 | 623.069 | 714.5669 | 934.6035
0
0
0
0
0
0
0

## LV-110V DC-PVC-AG
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder 110V DC PVC AG
|  |  |  | System Nominal Voltage |  |  | 0.11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  |  | 0.54
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  |  | Refer-Min CSA
|  |  |  | Voltage Drop |  |  | 5 | (%) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  |  | 240
|  |  |  | Wiring System |  |  | DC-2W |  |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  |  | A/G
[10 empty] | Insulation Type |  |  | PVC/PVC |  |  | Base Temperature (A/G) |  |  |  | 50
[10 empty] | Number of Cores |  |  | 2C |  |  | Base Temperature (U/G) |  |  |  | 35 |  |  | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240
Nominal Ampacity (A) |  |  | 30 | 40 | 51 | 70 | 94 | 119 | 148 | 180 | 232 | 282 | 328 | 379 | 434 | 514 | [5 empty] | Page 106 of LV Abhar
Resistance (ohm/km) |  |  | 8.87 | 5.52 | 3.69 | 2.19 | 1.38 | 0.87 | 0.627 | 0.464 | 0.321 | 0.232 | 0.184 | 0.15 | 0.1205 | 0.0928 | [5 empty] | Page 6 of LV Cable Abhar
Reactance (ohm/km)
Derated Ampacity (A) |  |  | 16.2 | 21.6 | 27.54 | 37.8 | 50.76 | 64.26 | 79.92 | 97.2 | 125.28 | 152.28 | 177.12 | 204.66 | 234.36 | 277.56 | 0 | 0 | 0 | 0 | 0
Output | Full Load | Min. | Maximum Cable Run (m)
kW | A | CSA
0.1 | 0.90909 | 2.5 | 341.0372 | 548.0072 | 819.7832 | 1381.2785 | 2192.029 | 3477.0115 | 4824.5614 | 6519.3966 | 9423.676 | 13038.7931 | 16440.2174 | 20166.6667 | 25103.7344 | 32596.9828
0.5 | 4.5455 | 2.5 | 68.2074 | 109.6014 | 163.9566 | 276.2557 | 438.4058 | 695.4023 | 964.9123 | 1303.8793 | 1884.7352 | 2607.7586 | 3288.0435 | 4033.3333 | 5020.7469 | 6519.3966
1 | 9.0909 | 2.5 | 34.1037 | 54.8007 | 81.9783 | 138.1279 | 219.2029 | 347.7011 | 482.4561 | 651.9397 | 942.3676 | 1303.8793 | 1644.0217 | 2016.6667 | 2510.3734 | 3259.6983
1.5 | 13.6364 | 2.5 | 22.7358 | 36.5338 | 54.6522 | 92.0852 | 146.1353 | 231.8008 | 321.6374 | 434.6264 | 628.2451 | 869.2529 | 1096.0145 | 1344.4444 | 1673.5823 | 2173.1322
2 | 18.1818 | 2.5 |  | 27.4004 | 40.9892 | 69.0639 | 109.6014 | 173.8506 | 241.2281 | 325.9698 | 471.1838 | 651.9397 | 822.0109 | 1008.3333 | 1255.1867 | 1629.8491
0
0
0
0
0
0
0

## LV-24V DC-PVC-AG
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder 110V DC PVC AG
|  |  |  | System Nominal Voltage |  |  | 0.024 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  |  | 0.54
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  |  | Refer-Min CSA
|  |  |  | Voltage Drop |  |  | 5 | (%) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  |  | 240
|  |  |  | Wiring System |  |  | DC-2W |  |  | Rated Voltage |  |  | 0.6/1kV |  |  | Installation |  |  |  | A/G
[10 empty] | Insulation Type |  |  | PVC/PVC |  |  | Base Temperature (A/G) |  |  |  | 50
[10 empty] | Number of Cores |  |  | 2C |  |  | Base Temperature (U/G) |  |  |  | 35 |  |  | `
[10 empty] | Max Conductor Temp. |  |  | 90
Cable Size |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240
Nominal Ampacity (A) |  |  | 30 | 40 | 51 | 70 | 94 | 119 | 148 | 180 | 232 | 282 | 328 | 379 | 434 | 514 | [5 empty] | Page 106 of LV Abhar
Resistance (ohm/km) |  |  | 8.87 | 5.52 | 3.69 | 2.19 | 1.38 | 0.87 | 0.627 | 0.464 | 0.321 | 0.232 | 0.184 | 0.15 | 0.1205 | 0.0928 | [5 empty] | Page 6 of LV Cable Abhar
Reactance (ohm/km)
Derated Ampacity (A) |  |  | 16.2 | 21.6 | 27.54 | 37.8 | 50.76 | 64.26 | 79.92 | 97.2 | 125.28 | 152.28 | 177.12 | 204.66 | 234.36 | 277.56 | 0 | 0 | 0 | 0 | 0
Output | Full Load | Min. | Maximum Cable Run (m)
kW | A | CSA
0.1 | 4.1667 | 2.5 | 16.2345 | 26.087 | 39.0244 | 65.7534 | 104.3478 | 165.5172 | 229.6651 | 310.3448 | 448.5981 | 620.6897 | 782.6087 | 960 | 1195.0207 | 1551.7241
0.5 | 20.8333 | 2.5 |  | 5.2174 | 7.8049 | 13.1507 | 20.8696 | 33.1034 | 45.933 | 62.069 | 89.7196 | 124.1379 | 156.5217 | 192 | 239.0041 | 310.3448
1 | 41.6667 | 2.5 |  |  |  |  | 10.4348 | 16.5517 | 22.9665 | 31.0345 | 44.8598 | 62.069 | 78.2609 | 96 | 119.5021 | 155.1724
1.5 | 62.5 | 2.5 | [5 empty] | 11.0345 | 15.311 | 20.6897 | 29.9065 | 41.3793 | 52.1739 | 64 | 79.668 | 103.4483
2 | 83.3333 | 2.5 | [7 empty] | 15.5172 | 22.4299 | 31.0345 | 39.1304 | 48 | 59.751 | 77.5862
0
0
0
0
0
0
0

## LV-FDR-110V DC-PVC-AG Indoor (hidden)
CABLE SIZE SELECTION TABLE STATIC FEEDER
LV Feeder 110V DC PVC AG (Indoor)
|  |  |  | System Nominal Voltage |  |  | 0.11 | (kV) |  | Standard |  |  | IEC |  |  | Derating factor |  |  |  | 0.506
|  |  |  | System Frequency |  |  | 50 | (Hz) |  | Unit System |  |  | Metric |  |  | Min Cable Size |  |  |  | Refer-Min CSA
|  |  |  | Voltage Drop |  |  | 1 | (%) |  | Conductor Type |  |  | Cu |  |  | Max Cable Size |  |  |  | 240
|  |  |  | Wiring System |  |  | DC-2W |  |  | Rated Voltage |  |  | 0.45/0.75kV |  |  | Installation |  |  |  | A/G
[10 empty] | Insulation Type |  |  | PVC/PVC |  |  | Base Temperature (A/G) |  |  |  | 45
[10 empty] | Number of Cores |  |  | 2C |  |  | Base Temperature (U/G) |  |  |  | 30 |  | `
[10 empty] | Max Conductor Temp. |  |  | 70
Cable Size |  | Run | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3
|  | Size | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 150 | 185 | 240 | 185 | 240
Nominal Ampacity (A) |  |  | 30 | 40 | 51 | 70 | 94 | 119 | 148 | 180 | 232 | 282 | 328 | 379 | 434 | 514 | 758 | 868 | 1028 | 1302 | 1542
Resistance (ohm/km) |  |  | 9.045 | 5.623 | 3.721 | 2.201 | 1.388 | 0.878 | 0.633 | 0.468 | 0.323 | 0.233 | 0.184 | 0.151 | 0.119 | 0.0911 | 0.0755 | 0.0595 | 0.04555 | 0.039667 | 0.030367
Reactance (ohm/km)
Derated Ampacity (A) |  |  | 15.18 | 20.24 | 25.806 | 35.42 | 47.564 | 60.214 | 74.888 | 91.08 | 117.392 | 142.692 | 165.968 | 191.774 | 219.604 | 260.084 | 383.548 | 439.208 | 520.168 | 658.812 | 780.252
Output | Full Load | Min. | Maximum Cable Run (m)
kW | A | CSA
0.1 | 0.90909 | 2.5 | 66.8878 | 107.5938 | 162.5907 | 274.8751 | 435.879 | 689.0661 | 955.7662 | 1292.735 | 1873.065 | 2596.5665 | 3288.0435 | 4006.6225 | 5084.0336 | 6641.0538 | 8013.245 | 10168.0672 | 13282.1076 | 15252.1008 | 19923.1614
0.5 | 4.5455 | 2.5 | 13.3776 | 21.5188 | 32.5181 | 54.975 | 87.1758 | 137.8132 | 191.1532 | 258.547 | 374.613 | 519.3133 | 657.6087 | 801.3245 | 1016.8067 | 1328.2108 | 1602.649 | 2033.6134 | 2656.4215 | 3050.4202 | 3984.6323
1 | 9.0909 | 2.5 | 6.6888 | 10.7594 | 16.2591 | 27.4875 | 43.5879 | 68.9066 | 95.5766 | 129.2735 | 187.3065 | 259.6567 | 328.8043 | 400.6623 | 508.4034 | 664.1054 | 801.3245 | 1016.8067 | 1328.2108 | 1525.2101 | 1992.3161
1.5 | 13.6364 | 2.5 | 4.4592 | 7.1729 | 10.8394 | 18.325 | 29.0586 | 45.9377 | 63.7177 | 86.1823 | 124.871 | 173.1044 | 219.2029 | 267.1082 | 338.9356 | 442.7369 | 534.2163 | 677.8711 | 885.4738 | 1016.8067 | 1328.2108
2 | 18.1818 | 2.5 |  | 5.3797 | 8.1295 | 13.7438 | 21.7939 | 34.4533 | 47.7883 | 64.6368 | 93.6533 | 129.8283 | 164.4022 | 200.3311 | 254.2017 | 332.0527 | 400.6623 | 508.4034 | 664.1054 | 762.605 | 996.1581
0
0
0
0
0
0
0