## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0003-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1041 |  |  | Transmital Date: 06-Jun-2022
Document Title: Calculation Note For Cable Sizing |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1041 |  |  | Transmital Date: 06-Jun-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-CN-0003-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | 33KV is not applicable for gas compressor station and so pages 15 and 16 shall be modified. |  | BK-SUR-ENG-ELE-01-04755 | 2022-06-20 | ولتاژ 33 کیلوولت حذف گردید.
2 | Section 12.1, Gas Compressor C-2101: This cable is buried, but the derating factor has been selected from MV aboveground single core cables, It shall be rechecked and modified. (Shall be selected from MV underground three core cables.) Meanwhile according to above mentioned comments, the voltage drop calculation shall be modified and X,R shall be selected base on table. |  | BK-SUR-ENG-ELE-01-04755 | 2022-06-20 | ضریب کابل زیرزمینی برای فیدرهای MV به صورت سه سیمه برابر0.56 می باشد که اعمال گردید.
3 | Section 12.2, LV Transformer "GCS-TR-001" Primary Side: |  | BK-SUR-ENG-ELE-01-04755 | 2022-06-20
3-1 | The selected cable is 3 core, but derating factor has been selected base on MV aboveground single core cables. It shall be rechecked and modified. (Shall be selected from MV aboveground three core cables.) |  | BK-SUR-ENG-ELE-01-04755 | 2022-06-20 | مطابق با جدول صفحه 21 محاسبات ضریب کابل بصورت Above Ground , Three Core لحاظ گردید. در نتیجه ضریب کابل 0.61 خواهد بود که اعمال گردید.
3-2 | According to above mentioned comments, the voltage drop calculation shall be modified and X,R shall be selected base on table. |  | BK-SUR-ENG-ELE-01-04755 | 2022-06-20 | با توجه به اینکه کابل ها به صورت Above Ground و سه سیمه می باشند لذا ضرایب متناسب با شرایط قرار گیری کابل لحاظ شده است و مدرک محاسباتی به ررز گردید.
3-3 | According to above mentioned comments, following sentences shall be modified: -Since this cable is buried, it is considered as an under-ground cable which the de-rating factor is specified above and being 0.72. -So the minimum cable size that satisfied this condition is derived from equation (3), maximum cable length 250m and Cosφ =0.8 (Sin φ =0.6) |  | BK-SUR-ENG-ELE-01-04755 | 2022-06-20 | همانطور که در کامنت 3-1 توضیح داده شد، به علت اینکه این کابل بر روی سینی/نردبان و در هوا نصب می گردد، لذا کابل به صورت روزمینی و سه سیمه خواهد بود. در نتیجه ضرایب همگی تغییر یافت و مدرک به روزرسانی گردید.
4 | Section 12.2, LV Transformer "GCS-TR-001" Secondry Side: It shall be clarify why has not been selected 300 mm2 instead of 400 mm2 (It seems has been oversized and shall be modifed) |  | BK-SUR-ENG-ELE-01-04755 | 2022-06-20 | اعمال گردید.
5 | Related sheet for MV aboveground cable shall be added to attachement #1_Cable sizing chart. Meanwhile according to selected MV cable in cable sizing , the derating factor shall be selected base on MV underground/aboveground three core cables table. |  | BK-SUR-ENG-ELE-01-04755 | 2022-06-20 | اعمال گردید.
6 | This document shall be submitted as IFA after finalizing or minor comments on load list and network study. |  | BK-SUR-ENG-ELE-01-04755 | 2022-06-20 | در صورت وجود کامنتهای بیشتر این مدرک ویرایش می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 20-May-22 |  |  |  |  | Date: