## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-CN-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0879 |  |  | Transmital Date: 30-Apr-2022
Document Title: Calculation Note For Lighting System of Well Pads Security Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0879 |  |  | Transmital Date: 30-Apr-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-CN-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on architectural detail drawing for security building. |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | مدرک مطابق با آخرین ویرایش مدرک معماری اصلاح گردید و در صورت هر گونه تغییر این مدرک ویرایش خواهد شد.
2 | A seperat table shall be added to this document and shall be compared calculated Lux with IPS-E-EL-100 standard to check the result of calculation. |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | متن مربوط به مقایسه جدول استاندارد و محاسبات روشنایی اضافه گردید.
3 | Workplane/Value Chart shall be added to output reports for each room to check Emin/Emax. For example for resting area its about 0.096 that shall be modified in order to achieve uniform lighting. (u0 is 0.135) |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | تمامی نقشه های مورد نیاز اضافه گردید.
4 | The calculation shall be rechecked and modified from point of view the height of the rooms. It shall be rechecked again according to architectural detail drawing for security building. |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | با توجه به تغییر معماری ساختمان، این مدرک به روز گردید.
5 | Complementary comments will be submitted after received revised documents. |  | BK-SUR-ENG-ELE-01-04215 | 2022-05-10 | در صورت وجود هر گونه کامنت احتمالی تغییرات متعاقبا لحاظ خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 10-May-22 |  |  |  |  | Date: