## Sheet 4
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-SA-DB-0001 |  |  |  |  | EPC Contractor Tr. No :BK-HD-PEDCO-T-0093 |  |  | Transmital Date: 2021/08/14
Document Title: Active Fire Protection and Safety Concept |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-SA-TR-0093 |  |  | Transmital Date: 2021/08/14
[5 empty] | CRS No:NISOC-CRS- BK-GCS-PEDCO-120-SA-DB-0001-D00 |  |  | CRS Status: | C2
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | لازم است در بخش 3، استاندارد های ذیل اضافه گردد: 150- IPS-C-SF- 460- IPS-E-PR- 110- IPS-E-EL- 160- IPS-E-SF- BS-5839 - NFPA 20- NFPA12- |  | 00/2290/225647 | 1400/07/17 | اعمال گردید.
2 | در بخش های 5،2،8 و 8 متن از لحاظ پاراگراف بندی مورد بازنگری قرار داده شود. |  | 00/2290/225647 | 1400/07/17 | اعمال گردید.
3 | دربخش 13.2 صفحه 18 ، مدت زمان 4-6 ساعت ذکر گردد |  | 00/2290/225647 | 1400/07/17 | اعمال گردید.
4 | دربخش 13.6 و 13.7 ، فشار 10 بار ذکر گردد. |  | 00/2290/225647 | 1400/07/17 | اعمال گردید.
5 | دربخش 13.6 صفحه 20 ، حداکثر سرعت 3.5 متر بر ثانیه ذکر گردد |  | 00/2290/225647 | 1400/07/17 | اعمال گردید.
6 | دربخش 14.1.2 و 14.1.3 میزان پرتاب خاموش کننده های دستی و چرخدار پودری به ترتیب 1.5-6 و 3-7 متر ذکر گردد. |  | 00/2290/225647 | 1400/07/17 | اعمال گردید.
7 | لازم است در خصوص موارد ذیل توضیحات در مدرک اضافه گردد: |  | 00/2290/225647 | 1400/07/17 | _
7-1 | تجهیزات حفاظت فردی |  | 00/2290/225647 | 1400/07/17 | اعمال گردید.
7-2 | آموزش ایمنی |  | 00/2290/225647 | 1400/07/17 | اعمال گردید.
7-3 | الزامات ایمنی داخل اتاق کنترل و تجهیزات درون آن |  | 00/2290/225647 | 1400/07/17 | اعمال گردید.
7-4 | پروانه کار |  | 00/2290/225647 | 1400/07/17 | این مدرک جز رویه های اجرایی HSE می باشد که توسط بخش HSEگروه ساخت قبل از انجام هر کار تهیه و به تایید کارفرمای محترم می رسد.
7-5 | سایبان آتش نشانی |  | 00/2290/225647 | 1400/07/17 | اعمال گردید.
7-6 | cConsequence modeling , Hazop & Hazid |  | 00/2290/225647 | 1400/07/17 | قبلا در بخش 8.2 دیده شده است.
7-7 | منطقه تجمع ایمن |  | 00/2290/225647 | 1400/07/17 | اعمال و اضافه گردید.
7-8 | Flare Radiation & Study report |  | 00/2290/225647 | 1400/07/17 | به عنوان مدرکی مجزا در بخش فرآیند تهیه و ارسال می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: