## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-CN-0007_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0890 |  |  | Transmital Date: 01-May-2022
Document Title: Calculation Note For Earthing & Lightning System of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0890 |  |  | Transmital Date: 01-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-CN-0007_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | 5.4 Earth Conductor: Maximum short circuit level has been mentioned 68KA.!!! What is the reference of short circuit level? |  | BK-SUR-ENG-ELE-01-04252 | 2022-05-14 | اصلاح گردید.
2 | 6.1 Earthing Conductor Sizing According to our telephone conversation, the reference standard and vlaue of K, shall be modified base on IEC 60363-5-54 table A.54.2. |  | BK-SUR-ENG-ELE-01-04252 | 2022-05-14 | اصلاح گردید.
3 | 6.2 Calculation of Main Earthing Conductor at Substation: According to our telephone conversation, when short circuit current runs through ground loop, it will divide into two paths and consequently ground conductor shall tolerate only I/2=25KA. By using single core PVC insulated conductor in the switchgear building, k factor is 143 and therefore; S_min= (I √t)/k=(25000×√0.5)/143=124 A =150 mm2 (Earthing Loop at Substation) |  | BK-SUR-ENG-ELE-01-04252 | 2022-05-14 | این موضوع برای هادی بدون روکش دورتادور ساختمان پست صادق نمی باشد.
4 | 6.3 Rod Resistance: The soil resistivity of binak area shall be modified after finalizing or minor comments on geotechnical study. Meanwhile geotechnical study has not been submitted unitll now. Considerations shall be given that the well pads are in different location, but soil resistivity has been considered the same. |  | BK-SUR-ENG-ELE-01-04252 | 2022-05-14 | کزارش مطالعات خاک اضافه گردید و بر این اساس محاسبات به روزرسانی شد.
5 | Diesel generator and related local panel will be installed outdoor under shelter, so the earth loop calculation for diesel generator shelter shall be added. |  | BK-SUR-ENG-ELE-01-04252 | 2022-05-14 | شبکه رینگ اصلی سیستم ارت محاسبه گردیده است و تمامی تجهیزات بیرونی از قبیل استراکچرهای موجود، به این شبکه متصل می گردد.
6 | Outdoor area and equivalent resistor for power grounding system shall be added to this document. |  | BK-SUR-ENG-ELE-01-04252 | 2022-05-14 | محاسبات سیستم زمین مورد بازنگری قرار گرفته است.
7 | Calculation for grounding system for lightning protection system shall be added to this document. |  | BK-SUR-ENG-ELE-01-04252 | 2022-05-14 | محاسبه سیستم صاعقه گیر در ویرایش صفر نیز در مدرک وجود داشته است. با این حال مورد بازنگری قرار گرفته است.
8 | Following sentences on page 11 shall be deleted base on well pads scope of work and supply: But since there are 3 new power transformers, 3 electrodes will be considered in neutral point. These rods will provide main earth loop around substation which will be connected to main existing earth loop. |  | BK-SUR-ENG-ELE-01-04252 | 2022-05-14 | حذف گردید.
9 | Complementary comments will be submitted after received revised documents. |  | BK-SUR-ENG-ELE-01-04252 | 2022-05-14 | مدرک مورد بازنگری قرار گرفته است. در صورت وجود هر گونه کامنت آینده، این مدرک ویریایش خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 14-May-22 |  |  |  |  | Date: