## Sheet 1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-SA-PY-0001_D01 |  |  |  |  | EPC Contractor Tr. No : BK-HD-PEDCO-T-0865 |  |  | Transmital Date:27/APR/2022
Document Title: Fire Water Network Layout |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-SF-TR-0865 |  |  | Transmital Date:27/APR/2022
[5 empty] | CRS No: CRS-BK-GCS-PEDCO-120-SA-PY-0001_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | سایبان آتش نشانی جدید در ضلع شمال شرقی در نقشه نمایش داده شود. |  | 1401-2294-124173 | 1401/04/09 | در نظر گرفته شد.
2 | یک هایدارانت مانیتور بین HM-05 و HM-06 در نزدیکی TK-2101 اضافه گردد. |  | 1401-2294-124173 | 1401/04/09 | با توجه به حذف TK-2101 ،جابجا شدن پمپ های 2101A/B و همچنین چیدمان جدید نیازی به اضافه نمودن هایدرانت ماینتور در این محل نمی باشد.
3 | لازم است اتصال هدر پمپ های آتش نشانی از دو سر به رینگ آب آتش نشانی متصل باشد و چیدمان شیرهای جدا کننده به گونه ای لحاظ شود که امکان جدا کردن هدر پمپ ها از یک سمت امکان پذیر باشد. |  | 1401-2294-124173 | 1401/04/09 | در نظر گرفته شد و اصلاح گردید.
4 | طبق NOTE-23 نقشه P&ID-0023-03 می بایست رینگ جدید به رینگ موجود متصل گردد لذا هرگونه تمهیدات لازم جهت انجام اتصال شامل طراحی تفصیلی، خرید و اجرا در نظر گرفته شود. |  | 1401-2294-124173 | 1401/04/09 | با توجه به شرایط پیمان این موضوع جز SCOPE کاری نمی باشد لذا این مورد با توجه به در نظر گرفته اضافه کاری در مراحل بعدی پروژه در مدرک لحاظ گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: