## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W008N-PEDCO-110-PR-DT-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0808 |  |  | Transmital Date: 4/12/2022
Document Title: Process Data Sheets For Instrument Devices - W008N |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-0808 |  |  | Transmital Date: 4/12/2022
[5 empty] | CRS No: NISOC-CRS-BK-W008N-PEDCO-110-PR-DT-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | عطف به مفاد نامه شماره 1401/2294/43153 مورخ 1401/02/08 این امور در خصوص مدرک (P&ID-Extension of B/C Manifold)،لازم است تغییر فشار کاری خط لوله ورودی به چند راهه ، از فلنج بعد از شیر قطع اضطراری (ESDV) در نظر گرفته شود ، لذا می بایست فشار طراحی شیر ESDV متناسب با کلاس مربوطه درنظر گرفته شود ودر مدرک اعمال گردد. |  | 1401-2294-52764 | 1401/02/18 | کامنت مذکور بر روی مدرک Process Data Sheets For Instrument Devices - W007S & Extension Manifold اعمال گردید و در مدرک فوق موضوعیت ندارد.
2 | مطابق با بند فوق ، لازم است فشار طراحی مربوط به PG-1701/1702 , TRV-1701 مربوطه به تمامی خطوط جریانی نیز متناسب با کلاس مزبور در نظر گرفته شده و در مدرک فوق اعمال گردد . |  | 1401-2294-52764 | 1401/02/18 | رجوع شود به پاسخ بند 1 فوق
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: