## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR SAFETY EQUIPMENT
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 7
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | SA | DT | 0002 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR SAFETY EQUIPMENT نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | OCT.2022 |  | IFA |  |  |  | A.H.Saber |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | APR.2022 |  | IFC |  |  |  | A.H.Saber |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: |  |  | F0Z-708989
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR SAFETY EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 7
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | SA | DT | 0002 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 |  | X | [6 empty] | 70
7 |  | X | [6 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## EYE-WASH-SHOWER
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
DATA SHEETS FOR SAFETY EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 3 از 7
9184– 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA | DT |  | 0002 | D01
| GENERAL DATA | TYPE | [6 empty] | SAFETY SHOWER- Eye Wash
|  | VENDOR MODEL | [6 empty] | *
|  | QUANTITY | [6 empty] | BK-GCS-PEDCO-120-SA-MT-0001
|  | AREA CLASSIFICATION | [6 empty] | Note 4
|  | STANDARD | [6 empty] | ANSI,UNI
|  | DESIGN CODE | [6 empty] | ANSI,Z358.1
|  | INSTALLATION LOCATION | [6 empty] | OUTDOOR AND INDDOR ( BATTERY ROOM)
|  | TESTING | [6 empty] | PERFORMANCE , VISUAL & OPERATING
|  | FEEDING WATER TYPE | [6 empty] | POTABLE WATER
| PROCESS DATA | AMBIENT TEMPERATURE |  |  |  | ° C |  |  | Min. =5 Max. = 55
|  | HUMIDITY |  |  |  | % |  |  | Min. =12 Max. = 90
|  | ATMOSPHERE |  |  |  | mbar |  |  | 1013
|  | OPERATING TEMPERATURE |  |  |  | ° C |  |  | Amb.
|  | DESIGN TEMPERATURE |  |  |  | ° C |  |  | 85
|  | OPERATING PRESSURE |  |  |  | Barg |  |  | Min. = 2
|  | DESIGN PRESSURE |  |  |  | Barg |  |  | 7
|  | FLOW RATE |  |  |  | L/ min |  |  | 110 (for shower) 10 (for eye wash)
| TECHNICAL DATA | CONTROL | [6 empty] | FOOT PANEL FOR EYE WASH / HANDLE FOR SHOWER
|  | CONNECTOR/SIZE/TYPE | [6 empty] | FLANGE / 1½" /NPT DOWN UNION
|  | SHOWER VALVE TYPE | [6 empty] | BALL VALVE
|  | EYE WASH | [6 empty] | n YES o NO
|  | OVERHEAD TANK | [6 empty] | o YES n NO
|  | EYE WASH VALVE | [6 empty] | BALL VALVE
|  | BODY SPRAY | [6 empty] | n YES o NO
|  | HAND SHOWER | [6 empty] | n YES o NO
|  | SELF DRAIN SYSTEM | [6 empty] | n YES o NO
|  | FLOW REGULATOR | [6 empty] | n YES o NO
|  | SHUT OFF VALVE FOR WATER SUPPLY | [6 empty] | BALL VALVE, LOCKABLE
| DIMENSIONS | HEIGHT |  |  |  | mm |  |  | *
|  | WIDTH |  |  |  | mm |  |  | *
|  | DEPTH |  |  |  | mm |  |  | *
|  | WEIGHT |  |  |  | Kg |  |  | 11~14 / *
| MATERIAL OF CONSTRUCTION | STAND PIPE | [6 empty] | n GALVANIZED STEEL o STAINLESS STEEL
|  | SHOWER HEAD | [6 empty] | o CHROME PLATED BRASS n STAINLESS STEEL
|  | SHOWER VALVE | [6 empty] | n CHROME PLATED BRASS o STAINLESS STEEL
|  | EYE WASH VALVE | [6 empty] | n CHROME PLATED BRASS o STAINLESS STEEL
|  | FLOW REGULATOR | [6 empty] | n CHROME PLATED BRASS o STAINLESS STEEL
|  | EYE WASH | [6 empty] | n GALVANIZED STEEL o STAINLESS STEEL
|  | CHAIN | [6 empty] | n GALVANIZED STEEL o STAINLESS STEEL
|  | FOOT PANEL | [6 empty] | n GALVANIZED STEEL o STAINLESS STEEL
|  | COATING | [6 empty] | WITH 3 COAT OF ANTI- CORROSIVE PAINT
NOTES:
1: ALL INFORMATION MARKED BY (*) SHALL BE FILLED BY VENDOR.
2: SAFETY SHOWERS & EYE WASH STATION SHALL BE DESIGNED SUCH THAT WATER BEING DISCHARGED DOES NOT
EXCEED 38° C AND NOT FREEZED.
3: ANY DEVIATION FROM THIS DATASHEET SHALL BE BROUGHT TO THE ATTENTION OF THE PURCHASER FOR HIS APPROVAL.
4: AREA CLASIFICATION INSIDE BATTERY ROOM SHALL BE CONSIDERED ZONE1 - Exd IIC T3.
D01
D01
D01

## EYE-WASH-SHOWER (2)
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
DATA SHEETS FOR SAFETY EQUIPMENT
شماره پیمان: | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 7
9184– 073 - 053 | BK | GCS | PEDCO | 120 | SA | DT | 0002 | D01
D01

## SCBA
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
DATA SHEETS FOR SAFETY EQUIPMENT
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 5 از 7
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO |  | 120 | SA | DT |  | 0002 | D01
| GENERAL DATA | TYPE | [8 empty] | SCBA
|  | MODEL | [8 empty] | *
|  | QUANTITY |  |  |  |  | NO. |  |  |  | BK-GCS-PEDCO-120-SA-MT-0001
|  | SERVICE | [8 empty] | PERSONNEL PROTECTION
|  | DESIGN CODE | [8 empty] | NIOSH COMPLIANCE WITH NFPA 1981, US, OSHA FIRE BRIGADE REGULATION
|  | INSTALLATION LOCATION | [8 empty] | INDOOR
|  | SURFACE PROTECTION & PAINTING | [8 empty] | *
|  | TESTING | [8 empty] | PERFORMANCE & VISUAL & OPERATING
| PROCESS DATA | AMBIENT TEMPERATURE |  |  |  |  | ° C |  |  |  | Min. =5 Max. = 55
|  | DESIGN RELATIVE HUMIDITY |  |  |  |  | % |  |  |  | Max. = 90
|  | CYLINDER | BREATHING RATE |  |  |  | L/ Min |  |  |  | 40
|  |  | RATED SERVICE |  |  |  | Min |  |  |  | Min : 30 Max : 45
|  |  | VOLUME OF AIR |  |  |  | Lit |  |  |  | Min : 1200 Max : 1800
|  |  | ALARM | [7 empty] | n YES o NO
|  |  | SIZE | [7 empty] | *
| TECHNICAL DATA | CYLINDER | PRESSURE GAUGE | [7 empty] | n YES o NO
|  |  | PRESSURE REDUCER | [7 empty] | n YES o NO
|  |  | ALARM | [7 empty] | n YES o NO
|  |  | QUANTITY |  |  |  | NO. |  |  |  | 1 (NOTE 5)
|  |  | AIR PRESSURE | [7 empty] | POSITIVE
|  |  | MATERIAL | [7 empty] | *
|  |  | TYPE OF MASK | [7 empty] | FULL FACE MASK
|  |  | WEIGHT |  |  |  | Kg |  |  |  | Min : Max : *
|  | ACCESSORIES FOR THE COMPLETE SET | [8 empty] | TOOL KIT, MOLDED BREATHING APPARATUS CARRYING CASE RSM (RESCUE SECOND MASK) ATTACHMENT, AIR LINE ATTACHMENT, CAN OF DISINFECTANT *
Notes:
(1) ALL INFORMATION MARKED BY (*) SHALL BE FILLED BY VENDOR.
(2) ANY DEVIATION FROM THIS DATA SHEET MUST BE MADE OUTSTANDING & BROUGHT TO THE ATTENTION
OF THE COMPANY.
(3) AN ALARM WITH SOUND / VISUAL SIGN SHALL WARN USER BEFORE THE TIME OF SAFE PRESSURE DROP.
(4) WALL MOUNTED BRAKET FOR INSTALLATION ON WALL SHALL BE SUPPLY BY VENDOR
(5) ONE SPARE CYLINDER SHALL BE SUPPLIED.
(6) ANY DEVIATION FROM THIS DATASHEET SHALL BE BROUGHT TO THE ATTENTION OF THE PURCHASER FOR HIS APPROVAL.
(7) SUITABLE BOX SHALL BE CONSIDERED BY VENDOR FOR EQUIPMENT PROTECTION.
(8)STAINLESS STEEL (316 L) NAME PLATE SHALL BE PROVIDED BY VENDOR.

## FIRST-AID-KIT
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
DATA SHEETS FOR SAFETY EQUIPMENT
شماره پیمان: |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 7
9184– 073 - 053 |  | BK |  | GCS | PEDCO | 120 | SA | DT | 0002 | D01
| TYPE |  | FIRST AID KIT
| UNIT PER KIT |  | CONTENTS DESCRIPTION | [8 empty] | QTY.PER UNIT
| 1 |  | 2" BANDAGE COMPRESS | [8 empty] | 4
| 1 |  | 4"BANDAGE COMPRESS | [8 empty] | 1
| 1 |  | TRIANGULAR BANDAGE | [8 empty] | 1
| 1 |  | 24" X 72" ABSORBENT GAUZE | [8 empty] | 1
| 1 |  | 4" X 6 yd. GAUZE BANDAGE | [8 empty] | 1
| 1 |  | EYE DRESSING KIT | [8 empty] | 3
| 2 |  | 1" X 3 1/2" ADHESIVE STRIPS | [8 empty] | 16
| 1 |  | KNUCKLE COVERLETS | [8 empty] | 8
| 1 |  | AMMONIA INHALANTS | [8 empty] | 10
| 1 |  | MENTHOLATED SWABS | [8 empty] | 10
| 1 |  | 3 gm WATER WASH BURN CREAM | [8 empty] | 6
| 1 |  | BURN OINTMENT | [8 empty] | 1
| 1 |  | BURN DRESSING | [8 empty] | 10
| 1 |  | 3/4 oz. AEROCAINE AEROSOL | [8 empty] | 2
| 1 |  | TOURNIQUET | [8 empty] | 1
| 1 |  | METAL SPLINT | [8 empty] | 1
| 1 |  | WOUND CLEANING PADS | [8 empty] | 4
| 1 |  | STERILIZED COTTON | [8 empty] | 2
| 1 |  | SAVLON (BOTTLE) | [8 empty] | 1
Notes:
(1) BASIC REQUIREMENTS
The first aid shall have a wall- mountable of galvanized steel for convenient storage of medical supplies with a large enough door .
For easy access with spring catch and spring cushioned stop to protect against damage from abrupt opening. Lock should be Provided to prevent
unauthorized access.Cabinet shall have four shelves at staggered heights. Cabinet should have key hole & wall mounting brackets & clear glass. Each
kit should contain medicine & equipment as indicated here above.The first aid kit shall preferably meet the OSHA regulation 1917.58.
(2) EXTENT OF SUPPLY
Extent of supply will consist of the fabrication , painting & delivery of first aid kit including:
Cabinet
Medicine
Medical equipment
(3) EXPIRY DATE
All the limited life items should be usable for at least one year after delivery date.
(4) PAINTING
First aid kit cabinets shall be colored emerald green, shall bear red crescent logo.
(5) ANY DEVIATION FROM THIS DATASHEET SHALL BE BROUGHT TO THE ATTENTION OF THE PURCHASER FOR HIS APPROVAL.

## WIND SOCK
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR SAFETY EQUIPMENT
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 7
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | SA |  | DT | 0003 | D01
GENERAL DATA
| 1 | GENERAL INFORMATIONS
| 2 | TYPE | [7 empty] | WIND SOCK
| 3 | MODEL | [7 empty] | *
| 4 | QUANTITY | [7 empty] | AS PER MTO;BK-GCS-PEDCO-120-SA-MT-0001
| 5 | SERVICE | [7 empty] | SAFETY & FIRE FIGHTING
| 6 | INSTALLATION LOCATION | [7 empty] | OUTDOOR
| 7 | DESIGN CODE | [7 empty] | *
| 8 | PROCESS OPERATING DATA
| 9 | AMBIENT TEMP. MAX/MIN (°C) | [7 empty] | 55/5
| 10 | RELATIVE HUMIDITY MAX.(%) |  |  |  | MAX/MIN |  |  |  | 90
| 11 | RELATIVE HUMIDITY MIN.(%) |  |  |  | MAX/MIN |  |  |  | 12
| 12 | DESIGN STANDARD | [7 empty] | *
| 13 | APPROVING AUTHORITY | [7 empty] | *
| 14 | DESIGHN DATA
| 15 | WIND SOCK | COLOR | [6 empty] | ORANGE
| 16 |  | WEATHER RESISTANT | [6 empty] | YES - PLASTICIZED
| 17 |  | FIXING | [6 empty] | WINDSOCK FRAME
| 18 |  | CERTIFICATION AND APPROVALS | [6 empty] | *
| 19 |  | POWER | [6 empty] | *
| 20 |  | BASE | [6 empty] | 4 NOS- x 18MM HOLES ON 18 CM BOLT CIRCLE
| 21 |  | FINISH | [6 empty] | *
| 22 |  | LENS | [6 empty] | NO
| 23 |  | FLOODLIGHTS | [6 empty] | NO
| 24 |  | OBSTRUCTION LIGHT | [6 empty] | YES
| 25 | FRAME AND SUPPORT | SWIVEL ARRANGEMENT | [6 empty] | BALL BEARING SWIVEL
| 26 |  | SUPPORT TYPE | [6 empty] | ROOF/GROUND MOUNTED POST
| 27 |  | SUPPORT POST LENGTH | [6 empty] | APPROX.5000 MM
| 28 |  | SUPPORT AND MOUNTING | [6 empty] | POST WITH BASE PLATE
| 29 |  | FIXING ARRANGEMENT | [6 empty] | SUITABLE ON ROOF OR STANDING FRAME
| 30 | MATERIAL | WINDSOCK MATERIAL | [6 empty] | NYLON (OR SIMILAR)
| 31 |  | WINDSOCK FRAME, POLE MATERIAL/TYPE | [6 empty] | ALUMINUM/STAINLESS STEEL)
| 32 |  | BASE SUPPORT MATERIAL | [6 empty] | ALUMINUM/STAINLESS STEEL)
| 33 | DIMENSION
| 34 | LENGTH | [7 empty] | APPROX. 2400 MM
| 35 | DIAMETER | [7 empty] | APPROX. 460 MM
| 36 | HEIGHT | [7 empty] | 5000
| 37 | WEIGHT | [7 empty] | 42 IBS
| 38 | BASKET DIAMETER | [7 empty] | 450 MM
| 39 | BASKET LENGTH | [7 empty] | 600 MM
NOTE
1- ALL INFORMATION MARKED BY "*" SHALL BE FILLED BY VENDOR AND RETUNED DURING QUOTATION STAGE. 2- ALL MATERIAL OFFERED FOR THE ABOVE EQUIPMENT SHALL BE SUITABLE FOR USE IN THE ENVIRONMENTAL CONDITIONS SPECIFIED, INCLUDING FOR MARINE ENVIRONMENT, AND BE OF A TYPE CERTIFIED FOR USE ON PETROCHEMICAL INSTALLATIONS.
D01