## Cover
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 24
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | SA | DT | 0003 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEET FOR FIRFIGHTING EQUIPMENT
D01 |  | OCT.2022 |  | IFA |  |  |  | A.H.Saber |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | APR.2022 |  | IFC |  |  |  | A.H.Saber |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-708990
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 24
| 9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | SA | DT | 0003 |  | D01
REVISION RECORD SHEET
| page | D00 | D01 | D02 |  | D03 |  | D04 |  | page |  | D00 |  | D01 |  | D02 | D03 | D04
| 1 | X | X | [6 empty] | 65
| 2 | X | X | [6 empty] | 66
| 3 | X | X | [6 empty] | 67
| 4 | X | [7 empty] | 68
| 5 | X | X | [6 empty] | 69
| 6 | X | [7 empty] | 70
| 7 | X | X | [6 empty] | 71
| 8 | X | [7 empty] | 72
| 9 | X | X | [6 empty] | 73
| 10 | X | [7 empty] | 74
| 11 | X | X | [6 empty] | 75
| 12 | X | [7 empty] | 76
| 13 | X | X | [6 empty] | 77
| 14 | X | [7 empty] | 78
| 15 | X | [7 empty] | 79
| 16 | X | [7 empty] | 80
| 17 | X | X | [6 empty] | 81
| 18 | X | X | [6 empty] | 82
| 19 | X | [7 empty] | 83
| 20 | X | X | [6 empty] | 84
| 21 | X | [7 empty] | 85
| 22 | X | [7 empty] | 86
| 23 | X | X | [6 empty] | 87
| 24 | X | [7 empty] | 88
| 25 | [8 empty] | 89
| 26 | [8 empty] | 90
| 27 | [8 empty] | 91
| 28 | [8 empty] | 92
| 29 | [8 empty] | 93
| 30 | [8 empty] | 94
| 31 | [8 empty] | 95
| 32 | [8 empty] | 96
| 33 | [8 empty] | 97
| 34 | [8 empty] | 98
| 35 | [8 empty] | 99
| 36 | [8 empty] | 100
| 37 | [8 empty] | 101
| 38 | [8 empty] | 102
| 39 | [8 empty] | 103
| 40 | [8 empty] | 104
| 41 | [8 empty] | 105
| 42 | [8 empty] | 106
| 43 | [8 empty] | 107
| 44 | [8 empty] | 108
| 45 | [8 empty] | 109
| 46 | [8 empty] | 110
| 47 | [8 empty] | 111
| 48 | [8 empty] | 112
| 49 | [8 empty] | 113
| 50 | [8 empty] | 114
| 51 | [8 empty] | 115
| 52 | [8 empty] | 116
| 53 | [8 empty] | 117
| 54 | [8 empty] | 118
| 55 | [8 empty] | 119
| 56 | [8 empty] | 120
| 57 | [8 empty] | 121
| 58 | [8 empty] | 122
| 59 | [8 empty] | 123
| 60 | [8 empty] | 124
| 61 | [8 empty] | 125
| 62 | [8 empty] | 126
| 63 | [8 empty] | 127
| 64 | [8 empty] | 128

## HYDRANT
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: | [6 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  |  | نوع مدرک |  |  |  | سریال |  |  | نسخه |  |  | شماره صفحه: 3 از 24
9184 – 073 - 053 | [6 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | SA |  |  | DT |  |  |  | 0003 |  |  | D01
HYDRANT
| GENERAL DATA | VENDOR'S MODEL | [9 empty] | *
|  | TYPE | [9 empty] | oUNDERGROUND □ DRY BARREL
■WET BARREL ■PILLAR
|  | QUANTITY No. | [9 empty] | As per MTO; BK-GCS-PEDCO-120-SA-MT-0001
|  | LOCATION | [9 empty] | OUTDOOR
|  | REFERENCE DOCUMENT | [9 empty] | As per Specification For Fire Fighting Equipment; BK-GNRAL-PEDCO-000-SA-SP-0001
OPERATING CONDITIONS
| AMBIENT TEMPERATURE | [10 empty] | °C | [6 empty] | Min. = 5 Max. = 50
| HUMIDITY | [10 empty] | % | [6 empty] | MIN. =12 MAX. = 90
| ATMOSPHERE | [10 empty] | bara | [6 empty] | 1013
| FLUID HANDLED | [17 empty] | FIRE WATER
| FLUID TEMPERATURE | [10 empty] | °C | [6 empty] | OPERATING= Amb DESIGN= 85
| OPERATING PRESSURE | [10 empty] | barg | [6 empty] | Norm. = 10.4 Min.= 7 Design= 15
| FIRE RING MAIN | [17 empty] | oABOVEGROUND nUNDERGROUND
DESCRIPTION-ACCESSORIES
| STANDARD | [17 empty] | n NFPA n NIOEC
| DRAINAGE | [6 empty] | SELF DRAINAGE | [6 empty] | □ | YES |  |  |  | ■ |  | NO |  |  |  | □ TYPE: AUTO BLEED VALVE
| CONNECTION TO FIRE MAIN |  | FLANGE | [15 empty] | ■4" o 6"
|  |  | RATING | [15 empty] | 150 #,FF
|  |  | CONNECTION CODE | [15 empty] | ASME B16.5
|  |  | ADJUSTMENT PIPE | [15 empty] | n |  | YES |  |  | o |  | NO
| PUMPER CONNECTION |  | Not Required
| MAIN VALVE | [17 empty] | n |  | YES |  |  |  | o |  | NO
| COUPLINGS | QUANTITY | [16 empty] | 2
|  | STANDARD | [16 empty] | BS 336
|  | DIMENSION |  |  |  | o | [8 empty] | o |  |  |  | n |  | 2*2 1/2" |  |  |  |  | o
|  | TYPE |  |  |  | n | [5 empty] | Threaded |  |  | o | Inst. |  |  | o |  | Sym. |  |  |  |  | o |  | MALE |  | n | FEMALE
|  | ORIENTATION | [16 empty] | 180°(BETWEEN TWO HOSE CONNECTION)
|  | VALVE | [16 empty] | n |  | YES |  |  |  | o |  | NO
|  | LEVEL FROM GRADE | [16 empty] | HYDRANT SHALL BE 1100 mm ABOVE GROUND LEVEL
LANDING VALVE
| CONNECTION | INLET |  | DIMENSION | [18 empty] | TYPE |  |  |  |  | SOLID WEDGE GATE VALVE
|  |  |  | TYPE | n |  | Threaded |  |  | Threaded |  |  |  | o | Inst. |  | o |  | MALE |  |  | n FEMALE | MATERIAL |  |  |  |  | GUNMETAL
|  | OUTLET |  | DIMENSION | [18 empty] | QUANTITY |  |  |  |  | 2
|  |  |  | TYPE | o |  | Threaded |  |  | Threaded |  |  |  | n | Inst. |  | o |  | MALE |  |  | n FEMALE | CODE |  |  |  |  | BS5041
SAFETY
| BREAK POINT | [17 empty] | o |  | YES |  |  |  | o |  | NO |  |  | *
| AUTOMATIC CHECK | [17 empty] | o |  | YES |  |  |  | o |  | NO |  |  | *
| ACCESSORIES | [17 empty] | o | PLUGS |  |  | ■ |  | CHAIN |  |  |  | ■ | WRENCH
[23 empty] | o |  | COVER |  |  |  | ■ | CAP
D01
D01
D01
D01
D01

## HYDRANT (2)
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 4 از 24
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | SA | DT |  | 0003 | D01
HYDRANT
MATERIAL-PAINTING-TESTS
| BODY | [6 empty] | CAST IRON
| HYDRANT NOZZLE | [6 empty] | BRASS
| COUPLINGS | [6 empty] | ---
| PLUG-CHAIN | [6 empty] | C.S. GALVANIZED
| CAP | [6 empty] | BRASS
| PAINTING | [6 empty] | RED (RAL 3000)
| TEST | [6 empty] | VISUAL / PERFORMANCE
REMARKS
Notes:
(1) ALL INFORMATION MARKED BY (*) SHALL BE FILLED BY VENDOR.
(2) LANDING VALVE AND RELEVANT COUPLING SHALL BE BS 5041.
(3) PUMPER NOZZLE ORIENTATION SHALL BE TOWARD ROAD SIDE OR ACCESS WAY.
(4) HYDRANT SHALL BE RATED FOR WORKING PRESSURE OF 150 PSI. SEAT & BARREL SHALL BE TESTED AT PRESSURE OF 300 PSI.
(5) ANY DEVIATION FROM THIS DATASHEET SHALL BE BROUGHT TO THE ATTENTION OF THE PURCHASER FOR HIS APPROVAL.

## HYDRANT-WITH-TOP-MOUNTED
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: |  |  |  |  | پروژه |  | بسته کاری | صادرکننده |  | تسهیلات |  |  | رشته |  |  |  | نوع مدرک |  | سریال | نسخه |  |  | شماره صفحه: 5 از 24
9184 – 073 - 053 |  |  |  |  | BK |  | GCS | PEDCO |  | 120 |  |  | SA |  |  |  | DT |  | 0003 | D01
HYDRANT (WITH TOP MOUNTED WATER MONITOR)
| GENERAL DATA | VENDOR'S MODEL | [15 empty] | *
|  | HYDRANT TYPE | [15 empty] | oUNDERGROUND □DRY BARREL
■WET BARREL nPILLAR
|  | QUANTITY | [7 empty] | NO. | [7 empty] | As per MTO; BK-GCS-PEDCO-120-SA-MT-0001
|  | LOCATION | [15 empty] | OUTDOOR
|  | REFERENCE DOCUMENT | [15 empty] | As per Specification For Fire Fighting Equipment; BK-GNRAL-PEDCO-000-SA-SP-0001
|  | MONITOR TYPE | [15 empty] | DOUBLE WHEELED
OPERATING CONDITIONS
| AMBIENT TEMPERATURE | [8 empty] | °C | [7 empty] | Min. =5 Max. = 50
| HUMIDITY | [8 empty] | % | [7 empty] | MIN. =12 MAX. = 90
| ATMOSPHERE | [8 empty] | bara | [7 empty] | 1013
| FLUID HANDLED | [16 empty] | FIRE WATER
| FLUID TEMPERATURE | [8 empty] | °C | [7 empty] | OPERATING= Amb DESIGN= 85
| OPERATING PRESSURE | [8 empty] | barg | [7 empty] | Norm.= 10.4 Min.= 7 Design= 15
| MONITOR WATER FOLW RATE | [8 empty] | 2000 LPM @ 7 BAR
| ROTATION RANGE | [8 empty] | VERTICAL -45 TO 80 HORIZONTAL 0 - 360
| FIRE RING MAIN | [16 empty] | oABOVEGROUND nUNDERGROUND
DESCRIPTION-ACCESSORIES
| STANDARD | [16 empty] | n NFPA 24 n NIOEC-SP-47-27
| DRAINAGE |  |  |  | SELF DRAINAGE |  |  |  |  | n |  | YES |  | o |  | NO |  | nTYPE : AUTO BLEED VALVE
| CONNECTION TO FIRE MAIN |  | FLANGE | [14 empty] | o4" n 6"
|  |  | RATING | [14 empty] | 150 #,FF
|  |  | CONNECTION CODE | [14 empty] | ASME/ANSI B16.5
|  |  | ADJUSTMENT PIPE | [14 empty] | n | YES | o |  | NO
| MONITOR CONNECTION |  | FLANGE | [14 empty] | o | 100 | o |  | 150 |  |  | n | 4" | o | 3"
|  |  | RATING | [14 empty] | 150#,RF
|  |  | CONNECTION CODE | [14 empty] | ASME/ANSI B16.1
| MAIN VALVE | [16 empty] | n | YES |  | o |  | NO
| COUPLINGS | QUANTITY | [15 empty] | * (NOTE 3)
|  | STANDARD | [15 empty] | BS 336
|  | DIMENSION | [5 empty] | o | [5 empty] | o |  |  |  | n | 2*2 1/2" |  |  | n |  |  |  | o
|  | TYPE | [5 empty] | n | Threaded |  |  |  |  | o |  | Inst. |  | o | Sym. |  |  | o |  | MALE |  | n | FEMALE
|  | ORIENTATION | [15 empty] | 180°(BETWEEN TWO HOSE CONNECTION)
|  | VALVE | [15 empty] | n | YES |  |  | o |  | NO
|  | LEVEL FROM GRADE | [15 empty] | HYDRANT SHALL BE 1300 mm ABOVE GROUND LEVEL
PUMPER CONNECTION
LANDING VALVE
| CONNECTION | INLET |  | DIMENSION | [13 empty] | TYPE |  |  | SOLID WEDGE GATE VALVE
|  |  |  | TYPE | n | Threaded |  | o | Inst. |  | o | MALE |  | n | FEMALE |  |  | MATERIAL |  |  | GUNMETAL
|  | OUTLET |  | DIMENSION | [13 empty] | QUANTITY |  |  | 2
|  |  |  | TYPE | o | Threaded |  | n | Inst. |  | o | MALE |  | n | FEMALE |  |  | CODE |  |  | BS5041
D01
D01
D01
D01
D01
D01

## HYDRANT-WITH-TOP-MOUNTED (2)
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه |  | شماره صفحه: 6 از 24
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 |  | SA | DT |  | 0003 | D01
HYDRANT (WITH TOP MOUNTED WATER MONITOR)
SAFETY
| BREAK POINT | [7 empty] | o | YES |  | o |  | NO
| AUTOMATIC CHECK | [7 empty] | o | YES |  | o |  | NO
| ACCESSORIES |  |  |  | o | PLUGS |  |  | n | CHAIN |  | n |  | WRENCH
[9 empty] | o | COVER |  | n |  | CAP
MATERIAL-PAINTING-TESTS
| BODY | [7 empty] | CAST IRON
| COUPLINGS | [7 empty] | ---
| HYDRANT NOZZLE | [7 empty] | BRASS
| PLUG-CHAIN | [7 empty] | C.S.GALVANIZED
| CAP | [7 empty] | BRASS
| PAINTING | [7 empty] | RED (RAL 3000)
| TEST | [7 empty] | VISUAL / PERFORMANCE
REMARKS
Notes:
(1) ALL INFORMATION MARKED BY (*) SHALL BE FILLED BY VENDOR.
(2) LANDING VALVE AND RELEVANT COUPLING SHALL BE BS 5041.
(3) 4" COUPLING SHALL BE EQUIPPED WITH ELBOW AND FLANGE IN ACCORDANCE WITH MONITOR CONNECTION.
(4) HYDRANT SHALL BE RATED FOR WORKING PRESSURE OF 150 PSI. SEAT & BARREL SHALL BE TESTED AT PRESSURE OF 300 PSI.
(5) ANY DEVIATION FROM THIS DATASHEET SHALL BE BROUGHT TO THE ATTENTION OF THE PURCHASER FOR HIS APPROVAL.

## CO2 PORTABLE 1
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 24
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA | DT | 0003 | D01
GENERAL DATA
1 | GENERAL INFORMATIONS
2 | TYPE | [5 empty] | CO2 PORTABLE EXTINGUISHER
3 | MODEL | [5 empty] | *
4 | QUANTITY | [5 empty] | AS PER MTO; BK-GCS-PEDCO-120-SA-MT-0001
5 | TAG NO. | [5 empty] | *
6 | CHARACTERISTIC CAPACITY (KG) | [5 empty] | 5 KG / *
7 | INSTALLATION LOCATION | [5 empty] | OUTDOOR
8 | DESIGN CODE | [5 empty] | NFPA-10/IPS-G-SF-126/BS 5423
9 | SERVICE | [5 empty] | FIRE FIGHTING
10 | METHOD OF OPERATION | [5 empty] | STORED PRESSURE- SELF EXPELLANT
11 | OPERATING DATA
12 | FIRE CLASS | [5 empty] | B\C
13 | EFFECTIVE DISCHARGE TIME (SEC) | [5 empty] | 8~30 / *
14 | STREAM HORIZONTAL RANGE (M) | [5 empty] | 1~2.5 / *
15 | STREAM VERTICAL RANGE (M) | [5 empty] | *
16 | STREAM DISCHARGE ANGLE (DEG) | [5 empty] | *
17 | RESIDUAL AFTER DISCHARGE (%) | [5 empty] | *
18 | AMBIENT TEMP. MAX/MIN (°C) | [5 empty] | 50/5
19 | RELATIVE HUMIDITY MAX.(%) |  |  | MAX/MIN |  |  | 90/12
20 | EXTINGUISHER AGENT TYPE | [5 empty] | CO2 PORTABLE EXTINGUISHER
21 | INITIAL CHARGE SUPPLIED BY | [5 empty] | VENDOR
22 | MIN. FIRE RATING | [5 empty] | *
23 | TECHNICAL DATA
24 | BOTTLE | SHAPE |  |  |  |  | CYLINDRICAL
25 |  | NOMINAL CAPACITY (LIT) |  |  |  |  | *
26 |  | POWDER CHARGE CAPACITY (KG) |  |  |  |  | *
27 |  | MATERIAL |  |  |  |  | CARBON STEEL
28 |  | THICKNESS (MM) |  |  |  |  | *
29 |  | OPERATING PRESSURE (KG/CM²g) |  |  |  |  | *
30 |  | DESIGN PRESSURE (KG/CM²g) |  |  |  |  | *
31 |  | TEST PRESSURE (KG/CM²g) |  |  |  |  | *
32 |  | SAFETY DEVICE TYPE |  |  |  |  | BURST DISK
33 |  | CALIBRATION PRESSURE (KG/CM²g) |  |  |  |  | *
34 |  | POWDER LOADING MOUTH SIZE (MM) |  |  |  |  | *
35 |  | SUCTION SYPHON |  |  |  |  | YES
36 |  | PLUG MATERIAL |  |  |  |  | *
37 |  | HANDLE |  |  |  |  | YES
38 |  | WALL SUPPORT BRACKET |  |  |  |  | YES
39 |  | SHELL DESIGN CODE |  |  |  |  | ASME SEC.VIII DIV.I, EUROPEAN STD.,
40 |  | PRESSURE INDICATOR |  |  |  |  | NO
41 | DISCHARGE VALVE | TYPE |  |  |  |  | QUICK OPENING SQUEEZE LEVER
42 |  | MODEL |  |  |  |  | *
43 |  | MATERIAL |  |  |  |  | *
44 |  | METHOD OF OPERATION |  |  |  |  | MANUAL BY HANDWHEEL
45 |  | SHUTTER TYPE |  |  |  |  | *
46 |  | SHUTTER MATERIAL |  |  |  |  | *
47 | * TO BE ADVISED BY VENDOR
48 | Note
49
50 | KG/CM² ~ 1 BAR
51
52
53
54
55
56
57
D01
D01

## CO2 PORTABLE 2
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 8 از 24
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA | DT | 0003 | D01
GENERAL DATA
1 | TECHNICAL DATA
2 | RIGID ARM | RIGID ARM MATERIAL |  |  |  |  | *
3 |  | CONE MATERIAL |  |  |  |  | *
4 |  | ORIENTING JOINT |  |  |  |  | *
5 | HOSE | TYPE |  |  |  |  | HIGH PRESSURE
6 |  | MATERIAL |  |  |  |  | SHALL CONTAIN A METAL WIRE BRAID ANDSHALL HAVE EITHER AN OUTER WRAPPING OF TIGHTLY WOVEN HIGH-GRADE YARN OR A COVER OF NATURAL OR SYNTHETIC RUBBER.
7 |  | NOMINAL DIAMETER |  |  |  |  | *
8 |  | LENGTH |  |  |  |  | *
9 |  | OPERATING PRESSURE |  |  |  |  | *
10 |  | BURSTING PRESSURE |  |  |  |  | *
11 |  | TEST PRESSURE |  |  |  |  | *
12 | HORN | TYPE |  |  |  |  | ANTISTATIC NON-CONDUCTIVE
13 |  | MATERIAL |  |  |  |  | *
14 |  | DIMENSIONS |  |  |  |  | *
15 | OVERALL DIMENSIONS
16 | TOTAL HEIGHT (MM) | [5 empty] | *
17 | MAX. WIDTH (MM) | [5 empty] | *
18 | TOTAL WEIGHT (CHARGED) (KG) | [5 empty] | *
19 | PAINTING AND SURFACE PROTECTION
20 | SURFACE PROTECTION | [5 empty] | *
21 | PAINTING | [5 empty] | EXTERNALLY BAKED PAINT IN BLACK COLOR RAL 9005
22 | TESTING
23 | TEST | [5 empty] | IPS INTERNATIONAL STANDARD, HYDRO TEST
24 | NO. OF EQUIPMENT TO BE TESTED | [5 empty] | ALL
25 | INSPECTION CODE/ STANDARD | [5 empty] | NFPA-10/IPS-G-SF-126
26 | ENCLOSURES
27 | GENERAL NOTES | [5 empty] | SEE BELOW - NOTE 7
28 | EQUIPMENT DRAWING | [5 empty] | *
29 | * TO BE ADVISED BY VENDOR
30 | NOTE
31 | 1- ALL INFORMATION MARKED BY "*" SHALL BE FILLED BY VENDOR AND RETURNED DURING QUOTATION STAGE
32 | 2- ANY DEVIATION FROM THIS DATASHEET SHALL BE MADE OUT-STANDING AND BROUGHT TO THE ATTENTION OF THE
33 | OWNER FOR HIS APPROVAL
34 | 3- IN CASE OF ANY CONFLICT BETWEEN THIS DATASHEET AND CODES/STANDARDS,THE MOST STRINGEST SHALL BE APPLIED.
35 | 4- MARKING TO INDICATE EXTINGUISHER SUITABILITY ACCORDING TO CLASS OF FIRE AND OPERATING INSTRUCTIONS,
36 | SHALL BE LOCATED ON THE FRONT OF THE EXTINGUISHER.
37 | 5- THE EXTINGUISHER SHALL BE RECHARGABLE TYPE, THEREFORE CHARGING ADAPTOR WITH INSTRUCTION MANUAL
38 | SHALL BE PROVIDED BY SUPPLIER.
39 | 6- FINISH COLOR OF EXTINGUISHERS,SHALL BE BLACK (RAL 9005).
40 | 7- A WEATHERPROOF CABINET SHALL BE PROVIDED TO INSTALL EXTINGUISHER INSIDE THAT. THIS CABINET WILL BE FIXED
41 | ON WHCP SHELTER. FIXING DEVICES SUCH AS BOLT& NUTS SHOULD BE PROVIDED BY VENDOR.
42 | 8-THE TAG NO. OF EACH ITEM SHALL BE ENGRAVED ON STAINLESS STEEL PLATE AND TO BE FIXED TO EXTINGUISHER.
43 | 9- BELOW CHARACTERISTICS SHALL BE ENGRAVED ON ALL OF EXTINGUISHERS:
44 | MANUFACTURER NAME
45 | WORKING PRESSURE
46 | TEST PRESSURE
47 | MANUFACTURED DATE
48 | FABRICATION YEAR
49 | CYLINDER FULL WEIGHT
50 | CYLINDER EMPTY WEIGHT
51
52
53
54
55
56

## CO2 WHEELED 1
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 9 از 24
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA | DT | 0003 | D01
GENERAL DATA
1 | GENERAL INFORMATIONS
2 | TYPE | [5 empty] | WHEELED CO2
3 | MODEL | [5 empty] | *
4 | QUANTITY | [5 empty] | AS PER MTO; BK-GCS-PEDCO-120-SA-MT-0001
5 | TAG NO. | [5 empty] | *
6 | CHARACTERISTIC CAPACITY (KG) | [5 empty] | 30 KG / *
7 | INSTALLATION LOCATION | [5 empty] | INDOOR/OUT DOOR
8 | DESIGN CODE | [5 empty] | NFPA10 /IPS-G-SF-126/BS 1866
9 | SERVICE | [5 empty] | FIRE FIGHTING
10 | OPERATING DATA
11 | FIRE CLASS | [5 empty] | B\C
12 | EFFECTIVE DISCHARGE TIME (SEC) | [5 empty] | 22 / *
13 | STREAM HORIZONTAL RANGE (M) | [5 empty] | MIN. 4 / *
14 | STREAM VERTICAL RANGE (M) | [5 empty] | MIN. 4 / *
15 | STREAM DISCHARGE ANGLE (DEG) | [5 empty] | *
16 | RESIDUAL AFTER DISCHARGE (%) | [5 empty] | LESS THAN 5% / *
17 | AMBIENT TEMP. MAX/MIN (°C) | [5 empty] | 50/5
18 | RELATIVE HUMIDITY MAX.(%) |  |  | MAX/MIN |  |  | 90/12
19 | EXTINGUISHER AGENT TYPE | [5 empty] | CARBON DIOXIDE
20 | INITIAL CHARGE SUPPLIED BY | [5 empty] | VENDOR
21 | TECHNICAL DATA
22 | BOTTLE | SHAPE |  |  |  |  | CYLINDRICAL
23 |  | NOMINAL CAPACITY (LIT) |  |  |  |  | *
24 |  | AGENT CHARGE CAPACITY (KG) |  |  |  |  | 30
25 |  | MATERIAL |  |  |  |  | CARBON STEEL
26 |  | THICKNESS (MM) |  |  |  |  | *
27 |  | OPERATING PRESSURE (BARG) |  |  |  |  | *
28 |  | DESIGN PRESSURE (BARG) |  |  |  |  | *
29 |  | TEST PRESSURE (BARG) |  |  |  |  | *
30 |  | SAFETY DEVICE TYPE |  |  |  |  | *
31 |  | CALIBRATION PRESSURE (BARG) |  |  |  |  | *
32 |  | SUCTION SYPHON |  |  |  |  | YES
33 |  | PLUG MATERIAL |  |  |  |  | BRASS
34 |  | HANDLE |  |  |  |  | YES
35 |  | WALL SUPPORT BRACKET |  |  |  |  | NO
36 |  | SHELL DESIGN CODE |  |  |  |  | ASME SEC. VIII DIV.I
37 |  | PRESSURE INDICATOR |  |  |  |  | YES
38 | DISCHARGE VALVE | TYPE |  |  |  |  | QUICK OPENING
39 |  | MODEL |  |  |  |  | *
40 |  | MATERIAL |  |  |  |  | BRASS
41 |  | METHOD OF OPERATION |  |  |  |  | SQUEEZE LEVER
42 | * TO BE ADVISED BY VENDOR
43 | Note
44
45 | KG/CM² ~ 1 BAR
46
47
48
49
50
51
52
D01
D01

## CO2 WHEELED 2
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 10 از 24
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA | DT | 0003 | D01
GENERAL DATA
1 | TECHNICAL DATA
2 | RIGID ARM | RIGID ARM MATERIAL |  |  |  |  | *
3 |  | CONE MATERIAL |  |  |  |  | *
4 | HOSE | TYPE |  |  |  |  | FLEXIBLE
5 |  | MATERIAL |  |  |  |  | SYNTHETIC RUBBER
6 |  | NOMINAL DIAMETER (MM) |  |  |  |  | *
7 |  | LENGTH (CM) |  |  |  |  | 600
8 |  | PIPE BURSTING PRESSURE (BARG) |  |  |  |  | *
9 |  | TEST PRESSURE (BARG) |  |  |  |  | *
10 | NOZZLE | TYPE |  |  |  |  | PISTOL
11 |  | MODEL |  |  |  |  | *
12 |  | MATERIAL |  |  |  |  | LIGHT ALLOY
13 |  | STREAM SHUTTING DEVICE |  |  |  |  | YES
14 |  | SUPPORT |  |  |  |  | YES
15 | TRAILER | TYPE |  |  |  |  | SINGLE AXLE
16 |  | MATERIAL |  |  |  |  | CARBON STEEL OR COLD ROLLED STEEL
17 |  | WHEEL TYPE |  |  |  |  | FULL RUBBER
18 |  | WHEEL SIZE |  |  |  |  | *
19 |  | HAND BAR |  |  |  |  | YES
20 |  | TOWING EYE |  |  |  |  | NO
21 | OVERALL DIMENSIONS
22 | TOTAL HEIGHT (MM) | [5 empty] | *
23 | MAX. WIDTH (MM) | [5 empty] | *
24 | TOTAL WEIGHT (KG) | [5 empty] | *
25 | ACCESSORIES
26 | SUPPORT-TYPE | [5 empty] | TWO SOLID TIRES
27 | SHEET COVER | [5 empty] | NO
28 | PAINTING & SURFACE PROTECTION | [5 empty] | YES
29 | INSCRIPTION-LANGUAGE | [5 empty] | ENGLISH/FARSI
30 | INSTALLATION METHOD | [5 empty] | WITH TRAILER
31 | TEST + INSPECTION
32 | TEST | [5 empty] | NFPA, HYDRO TEST
33 | NO. OF EQUIPMENT TO BE TESTED | [5 empty] | ALL
34 | INSPECTION SPECIFICATION | [5 empty] | NFPA-12
35 | NOTE
36 | 1- PLEASE REFER TO DOCUMENTS "MTO FOR FIRE EXTINGUISHERS & "FIRE FIGHTING AND SAFETY EQUIPMENT LAYOUT.
37 | 2- EXTINGUISHERS SHALL BE CLEARLY&PERMANENTLY MARKED WITH NAME OF MANUFACTURE OR TRADE
38 | MARK/PURCHASER,YEAR OF MANUFACTURE, CLASSIFICATION & RATING.
39
40 | REMARK :
41 | * SHALL BE FILLED BY VENDOR AND RETURNED DURING QUOTATION STAGE.
42
43

## POWDER PORTABLE 1
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 11 از 24
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | SA |  | DT | 0003 | D01
GENERAL DATA
| 1 | GENERAL INFORMATIONS
| 2 | TYPE | [7 empty] | PORTABLE DRY CHEMICAL POWDER
| 3 | MODEL | [7 empty] | *
| 4 | QUANTITY | [7 empty] | AS PER MTO; BK-GCS-PEDCO-120-SA-MT-0001
| 5 | CHARACTERISTIC CAPACITY (KG) | [7 empty] | 12 (PREFERABLE CAPACITY) / *
| 6 | INSTALLATION LOCATION | [7 empty] | OUTDOOR
| 7 | DESIGN CODE | [7 empty] | NFPA-10/IPS-G-SF-126/BS 5423-BSEN3
| 8 | SERVICE | [7 empty] | FIRE FIGHTING
| 9 | METHOD OF OPERATION | [7 empty] | CO2 CARTRIDGE INSIDE THE SHELL
| 10 | PROCESS OPERATING DATA
| 11 | FIRE CLASS | [7 empty] | B/C
| 12 | EFFECTIVE DISCHARGE TIME (SEC) | [7 empty] | 15-25 / *
| 13 | STREAM HORIZONTAL RANGE (M) | [7 empty] | 1.5-6 / *
| 14 | STREAM VERTICAL RANGE (M) | [7 empty] | *
| 15 | STREAM DISCHARGE ANGLE (DEG) | [7 empty] | *
| 16 | RESIDUAL AFTER DISCHARGE (%) | [7 empty] | *
| 17 | AMBIENT TEMP. MAX/MIN (°C) | [7 empty] | 50/5
| 18 | RELATIVE HUMIDITY MAX.(%) |  |  |  | MAX/MIN |  |  |  | 90/12
| 19 | EXTINGUISHER AGENT TYPE | [7 empty] | POTASSIUM BICARBONATE
| 20 | UL or ULC CLASSIFICATIONS | [7 empty] | *
| 21 | TECHNICAL DATA
| 22 | POWDER BOTTLE | SHAPE | [6 empty] | CYLINDRICAL
| 23 |  | NOMINAL CAPACITY (LIT) | [6 empty] | *
| 24 |  | POWDER CHARGE CAPACITY (KG) | [6 empty] | 12/ *
| 25 |  | MATERIAL | [6 empty] | *
| 26 |  | THICKNESS (MM) | [6 empty] | *
| 27 |  | OPERATING PRESSURE (KG/CM²g) | [6 empty] | *
| 28 |  | DESIGN PRESSURE (KG/CM²g) | [6 empty] | *
| 29 |  | TEST PRESSURE (KG/CM²g) | [6 empty] | *
| 30 |  | SAFETY DEVICE TYPE | [6 empty] | BURST DISK / *
| 31 |  | CALIBRATION PRESSURE (KG/CM²g) | [6 empty] | *
| 32 |  | POWDER LOADING MOUTH SIZE (MM) | [6 empty] | *
| 33 |  | SUCTION SYPHON | [6 empty] | YES
| 34 |  | PLUG MATERIAL | [6 empty] | *
| 35 |  | HANDLE | [6 empty] | YES
| 36 |  | WALL SUPPORT BRACKET | [6 empty] | YES
| 37 |  | SHELL DESIGN CODE | [6 empty] | ASME SEC. VIII DIV.1/ EN/ IRANIAN STANDARDS / *
| 38 |  | PRESSURE INDICATOR | [6 empty] | NO
| 39 | DISCHARGE VALVE | TYPE | [6 empty] | QUICK OPENING
| 40 |  | MODEL | [6 empty] | *
| 41 |  | METHOD OF OPERATION | [6 empty] | SQUEEZE LEVER / *
| 42 |  | MATERIAL | [6 empty] | *
| 43 |  | SHUTTER TYPE | [6 empty] | *
| 44 |  | SHUTTER MATERIAL | [6 empty] | *
| 45 | NOZZLE | TYPE | [6 empty] | FULL JET
| 46 |  | MODEL | [6 empty] | *
| 47 |  | MATERIAL | [6 empty] | *
| 48 |  | STREAM SHUTTING DEVICE | [6 empty] | YES
| 49 |  | STUPPORT | [6 empty] | YES
| 50 | * TO BE ADVISED BY VENDOR
| 51 | 1 KG/CM² ~ 1 BAR
D01
D01

## POWDER PORTABLE 2
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 12 از 24
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | SA | DT | 0003 | D01
GENERAL DATA
1 |  | TECHNICAL DATA
2 |  | PRESSERIZED BOTTLE | TYPE | [5 empty] | CARTRIDGE
3 |  |  | GAS TYPE | [5 empty] | CARBON DIOXIDE
4 |  |  | BOTTLE NOMINAL CAPACITY (LIT) | [5 empty] | *
5 | 5 |  | GAS CHARGE CAPACITY (KG) | [5 empty] | *
6 | 6 |  | BOTTLE MATERIAL | [5 empty] | *
7 | 6 |  | THICKNESS (MM) | [5 empty] | *
8 | 6 |  | OPERATING PRESSURE (KG/CM²g) | [5 empty] | *
9 | 6 |  | DESIGN PRESSURE (KG/CM²g) | [5 empty] | *
10 | 6 |  | TEST PRESSURE (KG/CM²g) | [5 empty] | *
11 | 6 |  | SAFETY DEVICE | [5 empty] | YES
12 | 6 |  | SAFETY DEVICE SET PRESSURE (KG/CM²g) | [5 empty] | *
13 | 6 |  | BOTTLE POSITION | [5 empty] | INTERNAL OF EXTINGUISHER
14 | 6 | HOSE | TYPE | [5 empty] | HIGH PRESSURE
15 | 6 |  | MATERIAL | [5 empty] | *
16 | 6 |  | NOMINAL DIAMETER (MM) | [5 empty] | NOT LESS THAN 9.5 MM
17 | 6 |  | LENGTH (M) | [5 empty] | *
18 | 6 |  | OPERATING PRESSURE (KG/CM²g) | [5 empty] | *
19 | 6 |  | BURSTING PRESSURE (KG/CM²g) | [5 empty] | *
20 | 6 |  | HYDROSTATIC TEST PRESSURE (KG/CM²g) | [5 empty] | *
21 | 6 | OVERALL DIMENSIONS
22 | 6 | TOTAL HEIGHT (MM) | [6 empty] | *
23 | 6 | MAX. WIDTH (MM) | [6 empty] | *
24 | 6 | TOTAL WEIGHT (CHARGED) (KG) | [6 empty] | *
25 | 6 | PAINTING AND SURFACE PROTECTION
26 | 6 | SURFACE PROTECTION | [6 empty] | *
27 | 6 | PAINTING | [6 empty] | FRENCH BLUE (RAL 5002)
28 | 6 | TESTING
29 | 6 | TEST | [6 empty] | IPS INTERNATIONAL STANDARD, HYDRO TEST
30 | 6 | NO. OF EQUIPMENT TO BE TESTED | [6 empty] | ALL
31 | 6 | INSPECTION CODE/ STANDARD | [6 empty] | NFPA-10/IPS-G-SF-126-BSEN3
32 | 6 | ENCLOSURES
33 | 6 | GENERAL NOTES | [6 empty] | SEE BELOW - NOTE 7
34 | 6 | EQUIPMENT DRAWING | [6 empty] | *
35 | 6 | * TO BE ADVISED BY VENDOR
36 | 6 | NOTE
37 | 6
38 | 6 | 1. ALL INFORMATION MARKED BY "*" SHALL BE FILLED BY VENDOR AND RETURNED DURING QUOTATION STAGE
39 | 6 | 2. ANY DEVIATION FROM THIS DATASHEET SHALL BE MADE OUT-STANDING AND BROUGHT TO THE ATTENTION OF THE
40 | 6 | OWNER FOR HIS APPROVAL
41 | 6 | 3.IN CASE OF ANY CONFLICT BETWEEN THIS DATASHEET AND CODES/STANDARDS,THE MOST STRINGEST SHALL BE APPLIED.
42 | 6 | 4. MARKING TO INDICATE EXTINGUISHER SUITABILITY ACCORDING TO CLASS OF FIRE AND OPERATING INSTRUCTIONS,
43 | 6 | SHALL BE LOCATED ON THE FRONT OF THE EXTINGUISHER.
44 | 6 | 5. THE EXTINGUISHER SHALL BE RECHARGABLE TYPE, THEREFORE CHARGING ADAPTOR WITH INSTRUCTION MANUAL
45 | 6 | SHALL BE PROVIDED BY SUPPLIER.
46 | 6 | 6. FINISH COLOR OF EXTINGUISHERS SHALL BE FRENCH BLUE (RAL 5002).
47 | 6 | 7. A WEATHERPROOF CABINET SHALL BE PROVIDED TO INSTALL EXTINGUISHER INSIDE THAT. THIS CABINET WILL BE FIXED
48 | 6 | ON WHCP SHELTER. FIXING DEVICES SUCH AS BOLT& NUTS SHOULD BE PROVIDED BY VENDOR.
49 | 6 | 8. THE TAG NO. OF EACH ITEM SHALL BE ENGRAVED ON STAINLESS STEEL PLATE AND TO BE FIXED TO EXTINGUISHER.
50 | 6 | 9. BELOW CHARACTERISTICS SHALL BE ENGRAVED ON ALL OF EXTINGUISHERS:
51 | 6 | MANUFACTURER NAME
52 | 6 | WORKING PRESSURE
53 | 6 | TEST PRESSURE
54 | 6 | MANUFACTURED DATE
55 | 6 | FABRICATION YEAR
56 | 6 | CYLINDER FULL WEIGHT
57 | 6 | CYLINDER EMPTY WEIGHT
58 | 6
59 | 6

## POWDER WHEELED 1
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 13 از 24
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 | SA |  | DT | 0003 | D01
GENERAL DATA
| 1 | GENERAL INFORMATIONS
| 2 | TYPE | [7 empty] | WHEELED DRY CHEMICAL POWDER
| 3 | MODEL | [7 empty] | *
| 4 | QUANTITY | [7 empty] | AS PER MTO; BK-GCS-PEDCO-120-SA-MT-0001
| 5 | CHARACTERISTIC CAPACITY (KG) | [7 empty] | 75/ *
| 6 | INSTALLATION LOCATION | [7 empty] | OUTDOOR
| 7 | DESIGN CODE | [7 empty] | NFPA-10/IPS-G-SF-126/BS 5423-EN1866
| 8 | SERVICE | [7 empty] | FIRE FIGHTING
| 9 | METHOD OF OPERATION | [7 empty] | CO2 CYLINDER, WHICH IS INTEGRAL TO THE STORAGE CYLINDER
| 10 | PROCESS OPERATING DATA
| 11 | FIRE CLASS | [7 empty] | B/C
| 12 | EFFECTIVE DISCHARGE TIME (SEC) | [7 empty] | 30~80 / *
| 13 | STREAM HORIZONTAL RANGE (M) | [7 empty] | 3-7 / *
| 14 | STREAM VERTICAL RANGE (M) | [7 empty] | *
| 15 | STREAM DISCHARGE ANGLE (DEG) | [7 empty] | *
| 16 | RESIDUAL AFTER DISCHARGE (%) | [7 empty] | LESS THAN 5% / *
| 17 | AMBIENT TEMP. MAX/MIN (°C) | [7 empty] | 50/5
| 18 | RELATIVE HUMIDITY MAX.(%) |  |  |  | MAX/MIN |  |  |  | 90/12
| 19 | EXTINGUISHER AGENT TYPE | [7 empty] | POTASSIUM BICARBONATE
| 20 | INITIAL CHARGE SUPPLIED BY | [7 empty] | *
| 21 | UL or ULC CLASSIFICATIONS | [7 empty] | 80 TO 640-B:C / *
| 22 | TECHNICAL DATA
| 23 | POWDER BOTTLE | SHAPE | [6 empty] | CYLINDRICAL
| 24 |  | NOMINAL CAPACITY (LIT) | [6 empty] | *
| 25 |  | OPERATING PRESSURE (KG/CM²g) | [6 empty] | *
| 26 |  | MATERIAL | [6 empty] | *
| 27 |  | THICKNESS (MM) | [6 empty] | *
| 28 |  | OPERATING PRESSURE (KG/CM²g) | [6 empty] | *
| 29 |  | OPERATING PRESSURE (KG/CM²g) | [6 empty] | *
| 30 |  | TEST PRESSURE (KG/CM²g) | [6 empty] | *
| 31 |  | SAFETY DEVICE TYPE | [6 empty] | BURST DISK
| 32 |  | CALIBRATION PRESSURE (KG/CM²g) | [6 empty] | *
| 33 |  | POWDER LOADING MOUTH SIZE (MM) | [6 empty] | *
| 34 |  | SUCTION SYPHON | [6 empty] | *
| 35 |  | PLUG MATERIAL | [6 empty] | *
| 36 |  | HANDLE | [6 empty] | YES
| 37 |  | WALL SUPPORT BRACKET | [6 empty] | NO
| 38 |  | SHELL DESIGN CODE | [6 empty] | ASME SEC. VIII DIV.1/ EN/ IPS / *
| 39 |  | PRESSURE INDICATOR | [6 empty] | NO
| 40 | DISCHARGE VALVE | TYPE | [6 empty] | HANDWHEEL
| 41 |  | MODEL | [6 empty] | *
| 42 |  | MATERIAL | [6 empty] | *
| 43 |  | METHOD OF OPERATION | [6 empty] | MANUAL BY HANDWHEEL
| 44 |  | SHUTTER TYPE | [6 empty] | *
| 45 |  | SHUTTER MATERIAL | [6 empty] | *
| 46 | HOSE | TYPE | [6 empty] | HIGH PRESSURE
| 47 |  | MATERIAL | [6 empty] | *
| 48 |  | NOMINAL DIAMETER (MM) | [6 empty] | *
| 49 |  | LENGTH (M) | [6 empty] | 15 / *
| 50 |  | OPERATING PRESSURE (KG/CM²g) | [6 empty] | 17 / *
| 51 |  | BURSTING PRESSURE (KG/CM²g) | [6 empty] | *
| 52 |  | HYDROSTATIC TEST PRESSURE (KG/CM²g) | [6 empty] | *
| 53 | * TO BE ADVISED BY VENDOR
| 54 | * 1 KG/CM² ~ 1 BAR
D01
D01

## POWDER WHEELED 2
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 14 از 24
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | SA | DT | 0003 | D01
GENERAL DATA
| 1 | TECHNICAL DATA
| 2 | PRESSERIZED BOTTLE | TYPE |  |  |  |  | CARTRIDGE
| 3 |  | GAS TYPE |  |  |  |  | CO2
| 4 |  | BOTTLE NOMINAL CAPACITY (LIT) |  |  |  |  | *
| 5 |  | GAS CHARGE CAPACITY (KG) |  |  |  |  | *
| 6 |  | BOTTLE MATERIAL |  |  |  |  | *
| 7 |  | THICKNESS (MM) |  |  |  |  | *
| 8 |  | OPERATING PRESSURE (KG/CM²g) |  |  |  |  | *
| 9 |  | DESIGN PRESSURE (KG/CM²g) |  |  |  |  | *
| 10 |  | TEST PRESSURE (KG/CM²g) |  |  |  |  | *
| 11 |  | SAFETY DEVICE |  |  |  |  | YES
| 12 |  | SAFETY DEVICE SET PRESSURE (KG/CM²g) |  |  |  |  | *
| 13 |  | BOTTLE POSITION |  |  |  |  | OUTSIDE OF EXTINGUISHER
| 21 | NOZZLE | TYPE |  |  |  |  | PISTOL
| 22 |  | MODEL |  |  |  |  | *
| 23 |  | MATERIAL |  |  |  |  | *
| 24 |  | STREAM SHUTTING DEVICE |  |  |  |  | YES
| 25 |  | SUPPORT |  |  |  |  | YES
| 26 | TRAILER | TYPE |  |  |  |  | *
| 27 |  | MATERIAL |  |  |  |  | *
| 28 |  | WHEEL TYPE |  |  |  |  | *
| 29 |  | WHEEL SIZE (MM) |  |  |  |  | *
| 30 |  | HAND BAR |  |  |  |  | YES
| 31 |  | TOWING EYE |  |  |  |  | NO
| 32 | OVERALL DIMENSIONS
| 33 | TOTAL HEIGHT (MM) | [5 empty] | *
| 34 | MAX. WIDTH (MM) | [5 empty] | *
| 35 | TOTAL WEIGHT (CHARGED) (KG) | [5 empty] | *
| 36 | PAINTING AND SURFACE PROTECTION
| 37 | SURFACE PROTECTION | [5 empty] | *
| 38 | PAINTING | [5 empty] | EXTERNALLY BAKED PAINT IN FRENCH BLUE RAL 5002
| 39 | TESTING
| 40 | TEST | [5 empty] | IPS INTERNATIONAL STANDARD, HYDRO TEST
| 41 | NO. OF EQUIPMENT TO BE TESTED | [5 empty] | ALL
| 42 | INSPECTION CODE/ STANDARD | [5 empty] | NFPA-10/IPS-G-SF-126-EN1866
| 43 | ENCLOSURES
| 44 | GENERAL NOTES | [5 empty] | NO NEED
| 45 | EQUIPMENT DRAWING | [5 empty] | *
| 46 | * TO BE ADVISED BY VENDOR
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64

## POWDER WHEELED 3
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIRE FIGHTING EQUIPMENT
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 15 از 24
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | SA | DT | 0003 | D01
1 | NOTE
2
3 | 1. ALL INFORMATION MARKED BY "*" SHALL BE FILLED BY VENDOR AND RETURNED DURING QUOTATION STAGE
4 | 2. ANY DEVIATION FROM THIS DATASHEET SHALL BE MADE OUT-STANDING AND BROUGHT TO THE ATTENTION OF THE
5 | OWNER FOR HIS APPROVAL.
6 | 3.IN CASE OF ANY CONFLICT BETWEEN THIS DATASHEET AND CODES/STANDARDS,THE MOST STRINGEST SHALL BE APPLIED.
7 | 4.MARKING TO INDICATE EXTINGUISHER SUITABILITY ACCORDING TO CLASS OF FIRE AND OPERATING INSTRUCTIONS,
8 | SHALL BE LOCATED ON THE FRONT OF THE EXTINGUISHER.
9 | 5.THE EXTINGUISHER SHALL BE RECHARGABLE TYPE, THEREFORE CHARGING ADAPTOR WITH INSTRUCTION MANUAL
10 | SHALL BE PROVIDED BY SUPPLIER.
11 | 6.FINISH COLOR OF EXTINGUISHERS SHALL BE FRENCH BLUE (RAL5002).
12 | 7. THE TAG NO. OF EACH ITEM SHALL BE ENGRAVED ON STAINLESS STEEL PLATE AND TO BE FIXED TO EXTINGUISHER.
13 | 8. BELOW CHARACTERISTICS SHALL BE ENGRAVED ON ALL OF EXTINGUISHERS:
14 | MANUFACTURER NAME
15 | WORKING PRESSURE
16 | TEST PRESSURE
17 | MANUFACTURED DATE
18 | FABRICATION YEAR
19 | CYLINDER FULL WEIGHT
20 | CYLINDER EMPTY WEIGHT
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56

## FIRE SHED
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR FIREFIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک |  | سریال | نسخه | شماره صفحه: 16 از 24
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA |  | DT |  | 0003 | D01
GENERAL DATA
| 1 | GENERAL INFORMATIONS
| 2 | item | [5 empty] | fire shed
| 3 | quantity | [5 empty] | AS PER MTO; |  | BK-GCS-PEDCO-120-SA-MT-0001
| 4 | [6 empty] | • Metal body closed on three sides
| 5 | [6 empty] | • Sloped roof
| 6 | [6 empty] | • Dimensions of 3*3*2.5
| 7 | [6 empty] | • Red colored
| 8 | general characteristics | [5 empty] | • Concrete floor
| 9 | [6 empty] | • Equipped with shelves (three levels)
| 10 | [6 empty] | • Equipped with lighting system
| 11 | [6 empty] | • Equipment List Panel
| 12 | [6 empty] | • Entrance slope way
| 13 | [6 empty] | • 10 No. 2 3/4" hoses 25 meters in length, (Based on BS336) • 1 NO. Foam Container Wrench, • 2 No. pick up tube + in line inductor (450LPM) • 2 No. Nozzles 10x ,(foam maker nozzle for process area), • 5 No. Concentrate Foam (FP 3%) containers -PVC (100 lit.) • 2 No. Dry chemical powder wheeled extinguisher 75 kg • 6 No. Dry chemical powder portable extinguisher 12 kg • 2 No. CO2 wheeled extinguisher 5 kg • 1 No. Foam Barrel Trailer • 1 No. Portable fire water monitor(2000LPM) • 2 NO. Water nozzles with three status (fog/jet/stop)
14
15
16
| 17 | containment
18
19
20
21
22
23
NOTE:
1-VENDOR shall also guarantee to replace without charge to Owner any or all parts defective due to faulty material, design or poor
workmanship for a period of 12 months from the date of commissioning.Also after-sales services of equipment for ten years after
successful operation will be done by Vendor/Manufacturer.
2. The container's shelves shall be made of wood.
3. For detail of extinguisher to be referred to 7 To 15
4. For details of other devices to be referred to sheet 17 To 24
D01
D01

## FIRE HOSE
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR FIREFIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 17 از 24
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA |  | DT | 0003 | D01
GENERAL DATA
| 1 | GENERAL INFORMATIONS
| 2 | TYPE | [5 empty] | FIRE HOSE
| 3 | SIZE | [5 empty] | 2,3/4" DIAMETER x 25 METER LENGTH
| 4 | MATERIAL | [5 empty] | DOUBLE JACKET OF LIGHT WEIGHT CONSTRUCTION. ALL CORDS IN JACKET SHALL BE NYLON FIBER AND JACKET SHALL BE IMPREGNATED WITH PVC NITRILE MATERIAL. INSIDE TUBE LINING TO BE NEOPRENE OR PVC NITRILE, AND BONDED TO JACKET.
5
6
7
8
| 9 | COLOR | [5 empty] | RED
| 10 | ACCESSORIES | [5 empty] | NONE
| 11 | TEST/INSPECTION | [5 empty] | VISUAL
| 12 | WEIGHT | [5 empty] | *
| 13 | INSTALLATION | [5 empty] | OUTDOOR
| 14 | OPERATING PRESSURE | [5 empty] | 7-11 BAR
| 15 | MODEL | [5 empty] | *
| 16 | SERVICE | [5 empty] | FIREFIGHTING
| 17 | INSTALLATION LOCATION | [5 empty] | OUTDOOR - INSIDE FIRESHED
| 18 | RATING | [5 empty] | 25 barg Minimum
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
| 48 | * TO BE ADVISED BY VENDOR
D01

## FOAM CONTAINER
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR FIREFIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 18 از 24
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA |  | DT | 0003 | D01
GENERAL DATA
| 1 | GENERAL INFORMATIONS
| 2 | TYPE | [5 empty] | FOAM CONTAINER
| 3 | MODEL | [5 empty] | *
| 4 | FOAM PERCENTAGE | [5 empty] | FP 3%
| 5 | CAPACITY | [5 empty] | 100 LITRE
| 6 | MATERIAL | [5 empty] | PVC
| 7 | COLOR | [5 empty] | *
| 8 | SERVICE | [5 empty] | FIREFIGHTING
| 9 | INSTALLATION LOCATION | [5 empty] | OUTDOOR - INSIDE FIRESHED
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
| 48 | * TO BE ADVISED BY VENDOR
D01

## PICK UP TUBE
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR FIREFIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 19 از 24
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA |  | DT | 0003 | D01
GENERAL DATA
| 1 | GENERAL INFORMATIONS
| 2 | TYPE | [5 empty] | FOAM PICK UP TUBE
| 3 | MODEL | [5 empty] | *
| 4 | SIZE | [5 empty] | 1200mm pick up hose / Venor to confirm
| 5 | MATERIAL | [5 empty] | ALUMINIUM/*
| 6 | FLOW CAPACITY | [5 empty] | 450 LPM
| 7 | SERVICE | [5 empty] | FOAM
| 8 | INSTALLATION LOCATION | [5 empty] | OUTDOOR - INSIDE FIRESHED
| 9 | APPROVAL | [5 empty] | *
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
| 43 | * TO BE ADVISED BY VENDOR

## NOZZLE 10X
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR FIREFIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 20 از 24
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA |  | DT | 0003 | D01
GENERAL DATA
| 1 | GENERAL INFORMATIONS
| 2 | TYPE | [5 empty] | FB 10 X
| 3 | MODEL | [5 empty] | *
| 4 | SIZE | [5 empty] | *
| 5 | MATERIAL | [5 empty] | ALUMINIUM/*
| 6 | FLOW CAPACITY | [5 empty] | 450 LPM
| 7 | EXPANSION RATIO | [5 empty] | 10/*
| 8 | OPERATING PRESSURE | [5 empty] | 10 BARG
| 9 | COLOR | [5 empty] | *
| 10 | SERVICE | [5 empty] | FOAM
| 11 | INSTALLATION LOCATION | [5 empty] | OUTDOOR - INSIDE FIRESHED
| 12 | APPROVAL | [5 empty] | *
| 13 | SPRAY / THROW RANGE | [5 empty] | 12/18 M
| 14 | FOAM PERCENTAGE | [5 empty] | 3%
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
| 46 | * TO BE ADVISED BY VENDOR

## INLINE INDUCTOR
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR FIREFIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 21 از 24
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA |  | DT | 0003 | D01
GENERAL DATA
| 1 | GENERAL INFORMATIONS
| 2 | TYPE | [5 empty] | INLINE INDUCTOR
| 3 | MODEL | [5 empty] | PORTABLE
| 4 | SERVICE | [5 empty] | FOAM
| 5 | INSTALLATION LOCATION | [5 empty] | OUTDOOR - INSIDE FIRESHED
| 6 | CAPACITY | [5 empty] | 450 LPM
| 7 | MATERIAL | [5 empty] | GUNMETAL/ *
| 8 | COLOR | [5 empty] | *
| 9 | FOAM PERCENTAGE | [5 empty] | FP 3%
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
| 48 | * TO BE ADVISED BY VENDOR

## BARREL TRAILER
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR FIREFIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 22 از 24
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA |  | DT | 0003 | D01
GENERAL DATA
| 1 | GENERAL INFORMATIONS
| 2 | TYPE | [5 empty] | BARREL TRAILER
| 3 | MANUFACTURER'S NAME | [5 empty] | *
| 4 | MANUFACTURER'S MODEL NO. | [5 empty] | *
| 5 | MODEL | [5 empty] | *
| 6 | SERVICE | [5 empty] | FIREFIGHTING
| 7 | INSTALLATION LOCATION | [5 empty] | OUTDOOR - INSIDE FIRESHED
| 8 | TECHNICAL DATA
| 9 | CAPACITY | [5 empty] | ONE BARREL
| 10 | MATERIAL | [5 empty] | *
| 11 | COLOR | [5 empty] | *
| 12 | AXLE TRAILER NO | [5 empty] | SINGLE
| 13 | AXLE TYPE | [5 empty] | *
| 14 | OVERALL DIMENSIONS
| 15 | TOTAL HEIGHT mm | [5 empty] | *
| 16 | MAX. HEIGHT AT INCLINED mm | [5 empty] | *
| 17 | MAX LENGTH mm | [5 empty] | *
| 18 | MAX. WIDTH mm | [5 empty] | *
| 19 | TOTAL WEIGHT KG | [5 empty] | *
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
| 51 | * TO BE ADVISED BY VENDOR

## PORTABLE MONITOR
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR FIREFIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 23 از 24
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA |  | DT | 0003 | D01
GENERAL DATA
| 1 | GENERAL INFORMATIONS
| 2 | TYPE | [5 empty] | HAND WHEELED PORTABLE MONITOR
| 3 | MODEL | [5 empty] | PORTABLE
| 4 | SERVICE | [5 empty] | FIREWATER
| 5 | INSTALLATION LOCATION | [5 empty] | OUTDOOR - INSIDE FIRESHED
| 6 | CAPACITY | [5 empty] | 2000 LPM
| 7 | MATERIAL | [5 empty] | *
| 8 | COLOR | [5 empty] | *
| 9 | QUICK DEPLOYMENT | [5 empty] | YES
| 10 | UNMANNED USE | [5 empty] | YES
| 11 | ROTATION | [5 empty] | 0 ~ 360 ° /*
| 12 | ELEVATION | [5 empty] | -20 ~ 80 ° /*
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
| 48 | * TO BE ADVISED BY VENDOR
D01
D01

## FOG JET STOP NOZZLE
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR FIREFIGHTING EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 24 از 24
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | SA |  | DT | 0003 | D01
GENERAL DATA
| 1 | GENERAL INFORMATIONS
| 2 | TYPE | [5 empty] | (FOG/JET/STOP) WATER NOZZLE
| 3 | MODEL | [5 empty] | *
| 4 | WATER CAPACITY | [5 empty] | 450 L/MIN
| 5 | INLET CONNECTION | [5 empty] | DUAL 2,1/2"
| 6 | MATERIAL | [5 empty] | STAINLESS STEEL OR BRONZE / GUNMETAL
| 7 | NET WEIGHT | [5 empty] | *
| 8 | NOZZLE | [5 empty] | MANUALLY ADJUSTABLE FROM JET TO FOG
| 9 | SLIDE BEARINGS | [5 empty] | WATER BALANCED FOR ROTATION AND ELEVATION
| 10 | SERVICE | [5 empty] | FIREWATER/FOAM
| 11 | INSTALLATION LOCATION | [5 empty] | OUTDOOR - INSIDE FIRESHED
| 12 | ORIFICE DIAMETER mm | [5 empty] | *
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
| 48 | * TO BE ADVISED BY VENDOR