## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DELUGE VALVES
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 4
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | SA | DT | 0004 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR DELUGE VALVES نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | OCT.2022 |  | IFA |  |  |  | A.H.Saber |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAR.2022 |  | IFA |  |  |  | A.H.Saber |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | JAN.2022 |  | IFC |  |  |  | A.H.Saber |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-708991
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DELUGE VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 4
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | SA | DT | 0004 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | [7 empty] | 67
4 | X | X | [6 empty] | 68
5 | [8 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## 3
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DELUGE VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه |  |  | شماره صفحه: 3 از 4
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | SA | DT |  | 0004 |  | D02
GENERAL DATA
| 1 | GENERAL INFORMATIONS
| 2 | TYPE | [5 empty] | SNAP ACTING, LATCHED TYPE, MANUAL LOCAL
| 3 | MODEL | [5 empty] | *
| 4 | QUANTITY | [5 empty] | 4
| 5 | TAG NO. | [5 empty] | DV-2301~2304
| 6 | INSTALLATION LOCATION | [5 empty] | DV-2301 For Slug Catcher Area
| 7 | [6 empty] | DV-2302 For Compressor Area-compressor Shelter 1
| 8 | [6 empty] | DV-2303 For Compressor Area-compressor Shelter 2
| 9 | [6 empty] | DV-2304 For Compressor Area-compressor Shelter 3
| 10 | DESIGN CODE | [5 empty] | NFPA 15 / IPS-E-SF-220
| 11 | SERVICE | [5 empty] | FIRE WATER
| 12 | PROCESS OPERATING DATA
| 13 | FLUID TYPE | [5 empty] | FIRE WATER
| 14 | AMBIENT TEMP. MAX/MIN (°C) | [5 empty] | 50/5
| 15 | RELATIVE HUMIDITY MAX.(%) | [5 empty] | 100
| 16 | OPERATING PRESSURE(MAX/NORM)(BARG) | [5 empty] | 2~10 / **
| 17 | DESIGN PRESSURE(BARG) | [5 empty] | 17 / **
| 18 | TEST PRESSURE(BARG) | [5 empty] | 22.5 /**
| 19 | TOTAL FLOW RATE(M3/Hr) | [5 empty] | DV-2301 | [5 empty] | 136.2 |  | m3/hr
| 20 | [6 empty] | DV-2302 | [5 empty] | 140.82 |  | m3/hr
| 21 | [6 empty] | DV-2303 | [5 empty] | 140.82 |  | m3/hr
| 22 | [6 empty] | DV-2304 | [5 empty] | 146.2 |  | m3/hr
TECHNICAL DATA
| 23 | HAZARD CLASSIFICATION | [5 empty] | ZONE(2), IIB,T3
| 24 | TOTAL DIFFERINTIAL PRESSURE(BARG) | [5 empty] | **
| 25 | SHUT-OFF DIFFERENTIAL PRESSURE(BARG) | [5 empty] | 10
| 26 | TECHNICAL DATA
| 27 | DELUGE VALVE | TYPE |  |  |  |  | SNAP ACTING, MANUAL OPERATION
| 28 |  | MODEL |  |  |  |  | SELF REGULATING TYPE (*)
| 29 |  | INLET CONNECTION TYPE/CODE |  |  |  |  | MATE TO R.F FLANGE ANSI B 16.5#150
| 30 | TECHNICAL DATA | DIAMETER (CONNECTION SIZE)/ RATING |  |  |  |  | DV-2301 |  | 4 | " | DV-2301 |  |  | 150 #
| 31 | [6 empty] | DV-2302 |  | 6 | " | DV-2302
| 32 | [6 empty] | DV-2303 |  | 6 | " | DV-2303
| 33 | [6 empty] | DV-2304 |  | 6 | " | DV-2304
* TO BE ADVISED BY VENDOR
** WILL BE SPECIFIED AFTER HYDRAULIC CALCULATION
D01
D01
D01
D01

## 4
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR DELUGE VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 4
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | SA | DT | 0004 | D02
TECHNICAL DATA
| 1 | SOLENOID VALVE | HAZARD CLASSIFICATION |  |  |  |  | ZONE 2, EEXD IIB
| 2 |  | NORMAL ACTION |  |  |  |  | ENERGIZED TO OPEN
| 3 |  | CODES |  |  |  |  | NEC, NFPA,
| 4 |  | BODY MATERIAL |  |  |  |  | *
| 5 |  | SUPPRESSION DIODE |  |  |  |  | YES
| 6 | ALARM DEVICE | TYPE |  |  |  |  | WATER MOTOR ALARM GONG
| 7 |  | MODEL |  |  |  |  | *
| 8 |  | QUANTITY |  |  |  |  | ONE PER EACH
| 9 |  | BODY MATERIAL |  |  |  |  | NON FERROUS
| 10 |  | SOUND TYPE |  |  |  |  | BELL
| 11 | PRESSURE SWITCH | TYPE |  |  |  |  | DPDT
| 12 |  | MODEL |  |  |  |  | *
| 13 |  | QUANTITY |  |  |  |  | ONE PER EACH
| 14 |  | CONTACT RATING/FORM |  |  |  |  | 24 VDC, 2A / DPDT
| 15 |  | ENCLOSURE |  |  |  |  | EEXD IIB T3, IP 65
| 16 |  | BODY MATERIAL |  |  |  |  | *
| 17 | OVERALL DIMENSIONS
| 18 | TOTAL LENGTH (MM) | [5 empty] | *
| 19 | TOTAL DEPTH (MM) | [5 empty] | *
| 20 | TOTAL HEIGHT (MM) | [5 empty] | *
| 21 | TOTAL. WEIGHT (KG) | [5 empty] | *
| 22 | WET WEIGHT (KG) | [5 empty] | *
| 23 | PAINTING AND SURFACE PROTECTION
| 24 | SURFACE PROTECTION | [5 empty] | *
| 25 | PAINTING | [5 empty] | EPOXY PRIMER ,WITH FIRE RED FINISHED
| 26 | [6 empty] | AS PER PROJECT SPECIFICATION BK-GNRAL-PEDCO-000-PI-SP-0006
| 27 | TESTING
| 28 | TEST | [5 empty] | IPS, INTERNATIONAL STANDARDS, HYDRO TEST PROCEDURE
| 29 | NO. OF EQUIPMENT TO BE TESTED | [5 empty] | ALL
| 30 | INSPECTION CODE/ STANDARD | [5 empty] | NFPA15/IPS-E-SF-220
| 31 | ENCLOSURES
| 32 | GENERAL NOTES | [5 empty] | SEE BELOW
| 33 | EQUIPMENT DRAWING | [5 empty] | *
| 34 | GUARANTEE AND WARRANTY
| 35 | GUARANTEE | [5 empty] | AS PER PMR For Deluge Valve & Water Spray
| 36 | AFTER SALE SERVICES | [5 empty] | AS PER PMR For Deluge Valve & Water Spray
| 1 | NOTE
| 2 | 1- ALL INFORMATION MARKED BY “*“SHALL BE FILLED BY VENDOR AND RETURNED DURING QUOTATION STAGE.
| 3 | 2- VALVE PILOT TRIM AS COMPLETE SET AND PREASSEMBLED WITHOUT SKID SHALL BE SUPPLIED BY VENDOR
| 4 | 3- IN CASE OF ANY CONFLICT BETWEEN THIS DATASHEET AND CODES/STANDARD, THE MOST STRINGENT SHALL BE APPLIED.
| 5 | 4- THE DELUGE VALVE SHALL BE PAINTED WITH RED COLOR RAL 3020 ACCORDING TO PROJECT PAINTING SPECIFICATION.
| 6 | 5- THE TAG NO. OF EACH ITEM SHALL BE ENGRAVED ON STAINLESS STEEL PLATE AND TO BE FIXED ON BODY.
| 7 | 6- ALL ELECTRICAL CONNECTIONS & CABLE GLAND SIZES SHALL BE INCONFORMITY WITH ISO STANDARD.
| 8 | 7- DELUGE VALVE COMPONENTS SHALL BE SUPPLIED BY VENDOR COMPLETELY AS PER PROJECT SPECIFICATIONS AND OTHER
| 9 | ACCESSORIES WHICH IS REQUIRED FOR PROPER OPERATION SUCH AS PRESSURE SWITCHES, PRESSURE GAUGES,
| 10 | THREE WAYS,BY PASS LINE, STRAINER, ISOLATION VALVE ON INLET/OUTLET AND BYPASS LINE,SOLENOID VALVE,
DRY PILOT ACTIVATION TRIM,SELF OUTLET PRESSURE REGULATING ACCESSORIES, RESTRICTION ORIFICE AND ETC.
| 11 | 8- DELUGE VALVE WITH PILOT AND VALVE TRIM COMPONENTS SHALL BE FABRICATED IN VENDOR’S SHOP AND AFTER FINAL
| 12 | PERFORMANCE TEST TO BE DELIVERED AS ASSEMBLED SET.
| 13 | 9- DELGE VALVES SHALL BE SKID MOUNTED AND EQUIPPED WITH ISOLATION AND DRAIN VALVE, ALSO ALL INSTRUMENT DEVICES
| 14 | SUCH AS PRESSURE SWITCHES AND SOLENOID VALVE SHALL BE SUPPLIED WITH CABLE GLAND.
| 15 | 10-OPENNING OF THE DELUGE VALVES SHALL BE TRIGGERD BY:
| 16 | • A LOCAL MANUAL (PUSH BOTTOM)CONTROL,
| 17 | • AN AUTOMATIC COMMAND FROM THE FIRE&GAS SYSTEM,
| 18 | • A MANUAL COMMAND (PUSH BOTTOM) FROM THE FIR & GAS PANEL THROUGH THE FIRE&GAS SYSTEM.
| 19 | DELUGE RELEASE SHALL AUTOMATICALLY TAKE PLACE UPON RECIEPT OF TRIGGERED SIGNAL. THE DELUGE VALVE SHALL BE
| 20 | RESET MANUALLY AND LOCALLY AFTER HAVING BEEN OPERATED.
| 21 | 11- DELUGE VALVE SHALL BE FM APPRIVED OR UM LISTED.
| 22 | 12- TO SET OUTLET PRESSURE FOR ANY DELUGE SYSTEM PLEASE REFERE TO HYDRAULIC CALCULATION REPORTS.
* TO BE ADVISED BY VENDOR
D01