## Sheet 4
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-SA-DT-0002 |  |  |  |  | EPC Contractor Tr. No :BK-HD-PEDCO-T-0842 |  |  | Transmital Date: 2022/04/19
Document Title: Data Sheets For Safety Equipment |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-SA-TR-0842 |  |  | Transmital Date: 2022/04/19
[5 empty] | CRS No:NISOC-CRS- BK-GCS-PEDCO-120-SA-DT-0002-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در صفحه 3 بند نوت 3 ، منطقه خطر Zone 1 درج گردد. |  | 01/2294/82959 | 1401/03/09 | اعمال گردید
2 | دردادخ برگ مربوط به چشم شوی قسمت کنترل ، دوش بصورت دستی فعال گردد و چشم شوی بصورت پدالی. همچنین نمای چشم شوی ودوش اضطراری مندرج در استاندارد ANSI Z358.1 به مدرک اضافه گردد. ( همراه با ابعاد) |  | 01/2294/82959 | 1401/03/09 | اعمال گردید
3 | در صفحه 4 وزن دستگاه 11 الی 14 کیلوگرم گزارش گردد. |  | 01/2294/82959 | 1401/03/09 | اعمال گردید
4 | لازم است داده برگ کلیه تجهیزات ایمنی از جمله بادنما ، دستگاه گاز سنج و ... به مدرک اضافه گردد. |  | 01/2294/82959 | 1401/03/09 | داده برگ بادنما اضافه گردید. داده های مربوط به شناساگرها دربخش ابزار دقیق صادر می گردند.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: