## WALL THICKNESS
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
WALL THICKNESS CALCULATION REPORT
شماره پیمان: | [6 empty] | پروژه |  | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 | [6 empty] | BK |  | GCS | PEDCO |  | 120 | PI | RT |  | 0006 |  | D02
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
AN01 |  | ASME B31.3 |  |  | Carbon Steel |  |  | CL.150 - PN 20, R.F. |  |  | 1 (mm) |  |  | - |  |  | - |  |  | - | 85 | - | 18.2 | D02
SERVICE |  | Oily Water, Diesel Oil, Nitrogen, Methanol
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.006 | 0.152 | 0.14 | 3.55 | 1 | 1.152 | 0.875 | 1.317 | 3.73 | Sch 80 | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.007 | 0.178 | 0.175 | 4.45 | 1 | 1.178 | 0.875 | 1.346 | 3.91 | Sch 80 | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.009 | 0.229 | 0.219 | 5.567 | 1 | 1.229 | 0.875 | 1.405 | 4.55 | Sch 80 | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.012 | 0.305 | 0.317 | 8.05 | 1 | 1.305 | 0.875 | 1.491 | 5.08 | Sch 80 | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.016 | 0.406 | 0.396 | 10.05 | 1 | 1.406 | 0.875 | 1.607 | 3.91 | Sch 40 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.023 | 0.584 | 0.583 | 14.817 | 1 | 1.584 | 0.875 | 1.81 | 5.49 | Sch 40 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.03 | 0.762 | 0.75 | 19.05 | 1 | 1.762 | 0.875 | 2.014 | 6.02 | Sch 40 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.043 | 1.092 | 1.104 | 28.05 | 1 | 2.092 | 0.875 | 2.391 | 7.11 | Sch 40 | 6
8 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.057 | 1.448 | 1.438 | 36.517 | 1 | 2.448 | 0.875 | 2.798 | 6.35 | Sch 20 | 8
10 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 10.75 | 273 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.071 | 1.803 | 1.792 | 45.5 | 1 | 2.803 | 0.875 | 3.203 | 6.35 | Sch 20 | 10
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
AN04 |  | ASME B31.3 |  |  | Carbon Steel |  |  | CL.150 - PN 20, R.F. |  |  | 3 (mm) |  |  | - |  |  | - |  |  | - | 85 | - | 18.2 | D02
SERVICE |  | Plant Air, Lean Glycol, Fire Water
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.006 | 0.152 | 0.14 | 3.55 | 3 | 3.152 | 0.875 | 3.602 | 3.73 | Sch 80 | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.007 | 0.178 | 0.175 | 4.45 | 3 | 3.178 | 0.875 | 3.632 | 3.91 | Sch 80 | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.009 | 0.229 | 0.219 | 5.567 | 3 | 3.229 | 0.875 | 3.69 | 4.55 | Sch 80 | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.012 | 0.305 | 0.317 | 8.05 | 3 | 3.305 | 0.875 | 3.777 | 5.08 | Sch 80 | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.016 | 0.406 | 0.396 | 10.05 | 3 | 3.406 | 0.875 | 3.893 | 5.54 | Sch 80 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.023 | 0.584 | 0.583 | 14.817 | 3 | 3.584 | 0.875 | 4.096 | 5.49 | Sch 40 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.03 | 0.762 | 0.75 | 19.05 | 3 | 3.762 | 0.875 | 4.299 | 6.02 | Sch 40 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.043 | 1.092 | 1.104 | 28.05 | 3 | 4.092 | 0.875 | 4.677 | 7.11 | Sch 40 | 6
8 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.057 | 1.448 | 1.438 | 36.517 | 3 | 4.448 | 0.875 | 5.083 | 6.35 | Sch 20 | 8
10 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 10.75 | 273 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.071 | 1.803 | 1.792 | 45.5 | 3 | 4.803 | 0.875 | 5.489 | 6.35 | Sch 20 | 10
12 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 12.75 | 323.8 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.084 | 2.134 | 2.125 | 53.967 | 3 | 5.134 | 0.875 | 5.867 | 6.35 | Sch 20 | 12
14 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 14 | 355.6 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.092 | 2.337 | 2.333 | 59.267 | 3 | 5.337 | 0.875 | 6.099 | 7.92 | Sch 20 | 14
16 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 16 | 406.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.105 | 2.667 | 2.667 | 67.733 | 3 | 5.667 | 0.875 | 6.477 | 7.92 | Sch 20 | 16
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
AN05 |  | ASME B31.3 |  |  | Killed Carbon Steel |  |  | CL.150 - PN 20, R.F. |  |  | 3 (mm) |  |  | NACE |  |  | PWHT |  |  | - | 85 | - | 18.2 | D02
SERVICE |  | Close Drain, Process Gas
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.006 | 0.152 | 0.14 | 3.55 | 3 | 3.152 | 0.875 | 3.602 | 3.73 | Sch 80 | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.007 | 0.178 | 0.175 | 4.45 | 3 | 3.178 | 0.875 | 3.632 | 3.91 | Sch 80 | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.009 | 0.229 | 0.219 | 5.567 | 3 | 3.229 | 0.875 | 3.69 | 4.55 | Sch 80 | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.012 | 0.305 | 0.317 | 8.05 | 3 | 3.305 | 0.875 | 3.777 | 5.08 | Sch 80 | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.016 | 0.406 | 0.396 | 10.05 | 3 | 3.406 | 0.875 | 3.893 | 5.54 | Sch 80 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.023 | 0.584 | 0.583 | 14.817 | 3 | 3.584 | 0.875 | 4.096 | 5.49 | Sch 40 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.03 | 0.762 | 0.75 | 19.05 | 3 | 3.762 | 0.875 | 4.299 | 6.02 | Sch 40 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.043 | 1.092 | 1.104 | 28.05 | 3 | 4.092 | 0.875 | 4.677 | 7.11 | Sch 40 | 6
8 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.057 | 1.448 | 1.438 | 36.517 | 3 | 4.448 | 0.875 | 5.083 | 6.35 | Sch 20 | 8
10 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 10.75 | 273 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.071 | 1.803 | 1.792 | 45.5 | 3 | 4.803 | 0.875 | 5.489 | 6.35 | Sch 20 | 10
12 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 12.75 | 323.8 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.084 | 2.134 | 2.125 | 53.967 | 3 | 5.134 | 0.875 | 5.867 | 6.35 | Sch 20 | 12
14 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 14 | 355.6 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.092 | 2.337 | 2.333 | 59.267 | 3 | 5.337 | 0.875 | 6.099 | 7.92 | Sch 20 | 14
16 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 16 | 406.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.105 | 2.667 | 2.667 | 67.733 | 3 | 5.667 | 0.875 | 6.477 | 7.92 | Sch 20 | 16
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
AN07 |  | ASME B31.3 |  |  | Killed Carbon Steel |  |  | CL.150 - PN 20, R.F. |  |  | 6 (mm) |  |  | NACE |  |  | PWHT |  |  | - | 85 | - | 18.2 | D02
SERVICE |  | Fuel Gas, Close Drain, Flare, Blow down, Process Gas
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.006 | 0.152 | 0.14 | 3.55 | 6 | 6.152 | 0.875 | 7.031 | 7.47 | Sch XXS | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.007 | 0.178 | 0.175 | 4.45 | 6 | 6.178 | 0.875 | 7.061 | 7.82 | Sch XXS | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.009 | 0.229 | 0.219 | 5.567 | 6 | 6.229 | 0.875 | 7.119 | 9.09 | Sch XXS | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.012 | 0.305 | 0.317 | 8.05 | 6 | 6.305 | 0.875 | 7.206 | 10.15 | Sch XXS | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.016 | 0.406 | 0.396 | 10.05 | 6 | 6.406 | 0.875 | 7.321 | 8.74 | Sch 160 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.023 | 0.584 | 0.583 | 14.817 | 6 | 6.584 | 0.875 | 7.525 | 7.62 | Sch 80 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.03 | 0.762 | 0.75 | 19.05 | 6 | 6.762 | 0.875 | 7.728 | 8.56 | Sch 80 | 4
6 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.043 | 1.092 | 1.104 | 28.05 | 6 | 7.092 | 0.875 | 8.105 | 10.97 | Sch 80 | 6
8 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.057 | 1.448 | 1.438 | 36.517 | 6 | 7.448 | 0.875 | 8.512 | 10.31 | Sch 60 | 8
10 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 10.75 | 273 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.071 | 1.803 | 1.792 | 45.5 | 6 | 7.803 | 0.875 | 8.918 | 9.27 | Sch 40 | 10
12 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 12.75 | 323.8 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.084 | 2.134 | 2.125 | 53.967 | 6 | 8.134 | 0.875 | 9.296 | 10.31 | Sch 40 | 12
14 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 14 | 355.6 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.092 | 2.337 | 2.333 | 59.267 | 6 | 8.337 | 0.875 | 9.528 | 11.13 | Sch 40 | 14
16 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 16 | 406.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.105 | 2.667 | 2.667 | 67.733 | 6 | 8.667 | 0.875 | 9.905 | 12.7 | Sch 40 | 16
18 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 18 | 457 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.118 | 2.997 | 3 | 76.167 | 6 | 8.997 | 0.875 | 10.282 | 11.13 | Sch 30 | 18
20 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 20 | 508 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.131 | 3.327 | 3.333 | 84.667 | 6 | 9.327 | 0.875 | 10.659 | 12.7 | Sch 30 | 20
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
AS00 |  | ASME B31.3 |  |  | Stainless Steel - 316L |  |  | CL.150 - PN 50, R.F. |  |  | 0 (mm) |  |  | - |  |  | - |  |  | - | 85 | - | 13.9 | D02
SERVICE |  | Chemical, Close drain
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 0.84 | 21.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.005 | 0.127 | 0.14 | 3.55 | 0 | 0.127 | 0.875 | 0.145 | 2.77 | Sch 40S | ½
¾ | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 1.05 | 26.7 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.006 | 0.152 | 0.175 | 4.45 | 0 | 0.152 | 0.875 | 0.174 | 2.87 | Sch 40S | ¾
1 | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 1.315 | 33.4 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.008 | 0.203 | 0.219 | 5.567 | 0 | 0.203 | 0.875 | 0.232 | 3.38 | Sch 40S | 1
1½ | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 1.9 | 48.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.011 | 0.279 | 0.317 | 8.05 | 0 | 0.279 | 0.875 | 0.319 | 3.68 | Sch 40S | 1½
2 | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 2.375 | 60.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.014 | 0.356 | 0.396 | 10.05 | 0 | 0.356 | 0.875 | 0.407 | 2.77 | Sch 10S | 2
3 | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 3.5 | 88.9 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.021 | 0.533 | 0.583 | 14.817 | 0 | 0.533 | 0.875 | 0.609 | 3.05 | Sch 10S | 3
4 | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 4.5 | 114.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.027 | 0.686 | 0.75 | 19.05 | 0 | 0.686 | 0.875 | 0.784 | 3.05 | Sch 10S | 4
6 | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 6.625 | 168.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.04 | 1.016 | 1.104 | 28.05 | 0 | 1.016 | 0.875 | 1.161 | 3.4 | Sch 10S | 6
8 | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 8.625 | 219.1 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.052 | 1.321 | 1.438 | 36.517 | 0 | 1.321 | 0.875 | 1.51 | 3.76 | Sch 10S | 8
10 | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 10.75 | 273 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.065 | 1.651 | 1.792 | 45.5 | 0 | 1.651 | 0.875 | 1.887 | 4.19 | Sch 10S | 10
12 | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 12.75 | 323.8 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.077 | 1.956 | 2.125 | 53.967 | 0 | 1.956 | 0.875 | 2.235 | 4.57 | Sch 10S | 12
14 | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 14 | 355.6 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.084 | 2.134 | 2.333 | 59.267 | 0 | 2.134 | 0.875 | 2.439 | 4.78 | Sch 10S | 14
16 | ASTM A312 Gr.TP316L | 85 | 185 | 13.9 | 201.7 | 16 | 406.4 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.096 | 2.438 | 2.667 | 67.733 | 0 | 2.438 | 0.875 | 2.786 | 4.78 | Sch 10S | 16
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
AZ00 |  | ASME B31.3 |  |  | Carbon Steel Galvanized |  |  | CL.150 - PN 20, R.F. |  |  | 0 (mm) |  |  | - |  |  | - |  |  | - | 85 | - | 18.2 | D02
SERVICE |  | Instrument Air<4”, Potable Water
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.006 | 0.152 | 0.14 | 3.55 | 0 | 0.152 | 0.875 | 0.174 | 3.73 | Sch 80 | ½
¾ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.007 | 0.178 | 0.175 | 4.45 | 0 | 0.178 | 0.875 | 0.203 | 3.91 | Sch 80 | ¾
1 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.009 | 0.229 | 0.219 | 5.567 | 0 | 0.229 | 0.875 | 0.262 | 4.55 | Sch 80 | 1
1½ | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.012 | 0.305 | 0.317 | 8.05 | 0 | 0.305 | 0.875 | 0.349 | 5.08 | Sch 80 | 1½
2 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.016 | 0.406 | 0.396 | 10.05 | 0 | 0.406 | 0.875 | 0.464 | 3.91 | Sch 40 | 2
3 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.023 | 0.584 | 0.583 | 14.817 | 0 | 0.584 | 0.875 | 0.667 | 5.49 | Sch 40 | 3
4 | ASTM A106 Gr.B | 85 | 185 | 18.2 | 264 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.03 | 0.762 | 0.75 | 19.05 | 0 | 0.762 | 0.875 | 0.871 | 6.02 | Sch 40 | 4
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
CN05 |  | ASME B31.3 |  |  | Killed Carbon Steel |  |  | CL.300 - PN 50, R.F. |  |  | 3 (mm) |  |  | NACE |  |  | PWHT |  |  | - | 155 | - | 47.7 | D02
SERVICE |  | Close Drain, Process Gas
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.014 | 0.356 | 0.14 | 3.55 | 3 | 3.356 | 0.875 | 3.835 | 4.78 | Sch 160 | ½
¾ | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.018 | 0.457 | 0.175 | 4.45 | 3 | 3.457 | 0.875 | 3.951 | 5.56 | Sch 160 | ¾
1 | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.022 | 0.559 | 0.219 | 5.567 | 3 | 3.559 | 0.875 | 4.067 | 6.35 | Sch 160 | 1
1½ | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.032 | 0.813 | 0.317 | 8.05 | 3 | 3.813 | 0.875 | 4.358 | 7.14 | Sch 160 | 1½
2 | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.041 | 1.041 | 0.396 | 10.05 | 3 | 4.041 | 0.875 | 4.618 | 5.54 | Sch 80 | 2
3 | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.06 | 1.524 | 0.583 | 14.817 | 3 | 4.524 | 0.875 | 5.17 | 5.49 | Sch 40 | 3
4 | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.077 | 1.956 | 0.75 | 19.05 | 3 | 4.956 | 0.875 | 5.664 | 6.02 | Sch 40 | 4
6 | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.113 | 2.87 | 1.104 | 28.05 | 3 | 5.87 | 0.875 | 6.709 | 7.11 | Sch 40 | 6
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
CN07 |  | ASME B31.3 |  |  | Killed Carbon Steel |  |  | CL.300 - PN 50, R.F. |  |  | 6 (mm) |  |  | NACE |  |  | PWHT |  |  | - | 155 | - | 47.7 | D02
SERVICE |  | Close Drain, Process Gas
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.014 | 0.356 | 0.14 | 3.55 | 6 | 6.356 | 0.875 | 7.264 | 7.47 | Sch XXS | ½
¾ | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.018 | 0.457 | 0.175 | 4.45 | 6 | 6.457 | 0.875 | 7.379 | 7.82 | Sch XXS | ¾
1 | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.022 | 0.559 | 0.219 | 5.567 | 6 | 6.559 | 0.875 | 7.496 | 9.09 | Sch XXS | 1
1½ | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.032 | 0.813 | 0.317 | 8.05 | 6 | 6.813 | 0.875 | 7.786 | 10.15 | Sch XXS | 1½
2 | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.041 | 1.041 | 0.396 | 10.05 | 6 | 7.041 | 0.875 | 8.047 | 8.74 | Sch 160 | 2
3 | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.06 | 1.524 | 0.583 | 14.817 | 6 | 7.524 | 0.875 | 8.599 | 11.13 | Sch 160 | 3
4 | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.077 | 1.956 | 0.75 | 19.05 | 6 | 7.956 | 0.875 | 9.093 | 11.13 | Sch 120 | 4
6 | ASTM A106 Gr.B | 155 | 311 | 47.7 | 691.9 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.113 | 2.87 | 1.104 | 28.05 | 6 | 8.87 | 0.875 | 10.137 | 10.97 | Sch 80 | 6
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
CS00 |  | ASME B31.3 |  |  | Stainless Steel - 316L |  |  | CL.300 - PN 50, R.F. |  |  | 0 (mm) |  |  | - |  |  | - |  |  | - | 155 | - | 30.3 | D02
SERVICE |  | Chemical, Close drain, Process Gas
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A312 Gr.TP316L | 155 | 311 | 30.3 | 439.5 | 0.84 | 21.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.011 | 0.279 | 0.14 | 3.55 | 0 | 0.279 | 0.875 | 0.319 | 2.77 | Sch 40S | ½
¾ | ASTM A312 Gr.TP316L | 155 | 311 | 30.3 | 439.5 | 1.05 | 26.7 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.014 | 0.356 | 0.175 | 4.45 | 0 | 0.356 | 0.875 | 0.407 | 2.87 | Sch 40S | ¾
1 | ASTM A312 Gr.TP316L | 155 | 311 | 30.3 | 439.5 | 1.315 | 33.4 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.017 | 0.432 | 0.219 | 5.567 | 0 | 0.432 | 0.875 | 0.494 | 3.38 | Sch 40S | 1
1½ | ASTM A312 Gr.TP316L | 155 | 311 | 30.3 | 439.5 | 1.9 | 48.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.025 | 0.635 | 0.317 | 8.05 | 0 | 0.635 | 0.875 | 0.726 | 3.68 | Sch 40S | 1½
2 | ASTM A312 Gr.TP316L | 155 | 311 | 30.3 | 439.5 | 2.375 | 60.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.031 | 0.787 | 0.396 | 10.05 | 0 | 0.787 | 0.875 | 0.899 | 2.77 | Sch 10S | 2
3 | ASTM A312 Gr.TP316L | 155 | 311 | 30.3 | 439.5 | 3.5 | 88.9 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.046 | 1.168 | 0.583 | 14.817 | 0 | 1.168 | 0.875 | 1.335 | 3.05 | Sch 10S | 3
4 | ASTM A312 Gr.TP316L | 155 | 311 | 30.3 | 439.5 | 4.5 | 114.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.059 | 1.499 | 0.75 | 19.05 | 0 | 1.499 | 0.875 | 1.713 | 3.05 | Sch 10S | 4
6 | ASTM A312 Gr.TP316L | 155 | 311 | 30.3 | 439.5 | 6.625 | 168.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.086 | 2.184 | 1.104 | 28.05 | 0 | 2.184 | 0.875 | 2.496 | 3.4 | Sch 10S | 6
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
FN05 |  | ASME B31.3 |  |  | Killed Carbon Steel |  |  | CL.600 - PN 50, R.F. |  |  | 3 (mm) |  |  | NACE |  |  | PWHT |  |  | - | 175 | - | 90 | D02
SERVICE |  | Hydrocarbon Gas
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.027 | 0.686 | 0.14 | 3.55 | 3 | 3.686 | 0.875 | 4.213 | 4.78 | Sch 160 | ½
¾ | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.033 | 0.838 | 0.175 | 4.45 | 3 | 3.838 | 0.875 | 4.386 | 5.56 | Sch 160 | ¾
1 | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.042 | 1.067 | 0.219 | 5.567 | 3 | 4.067 | 0.875 | 4.648 | 6.35 | Sch 160 | 1
1½ | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.06 | 1.524 | 0.317 | 8.05 | 3 | 4.524 | 0.875 | 5.17 | 7.14 | Sch 160 | 1½
2 | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.076 | 1.93 | 0.396 | 10.05 | 3 | 4.93 | 0.875 | 5.634 | 8.74 | Sch 160 | 2
3 | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.111 | 2.819 | 0.583 | 14.817 | 3 | 5.819 | 0.875 | 6.65 | 7.62 | Sch 80 | 3
4 | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.143 | 3.632 | 0.75 | 19.05 | 3 | 6.632 | 0.875 | 7.579 | 8.56 | Sch 80 | 4
6 | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.211 | 5.359 | 1.104 | 28.05 | 3 | 8.359 | 0.875 | 9.553 | 10.97 | Sch 80 | 6
8 | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.274 | 6.96 | 1.438 | 36.517 | 3 | 9.96 | 0.875 | 11.383 | 12.7 | Sch 80 | 8
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
FN07 |  | ASME B31.3 |  |  | Killed Carbon Steel |  |  | CL.600 - PN 50, R.F. |  |  | 6 (mm) |  |  | NACE |  |  | PWHT |  |  | - | 175 | - | 90 | D02
SERVICE |  | Hydrocarbon Gas
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 0.84 | 21.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.027 | 0.686 | 0.14 | 3.55 | 6 | 6.686 | 0.875 | 7.641 | 7.47 | Sch XXS | ½
¾ | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 1.05 | 26.7 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.033 | 0.838 | 0.175 | 4.45 | 6 | 6.838 | 0.875 | 7.815 | 7.82 | Sch XXS | ¾
1 | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 1.315 | 33.4 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.042 | 1.067 | 0.219 | 5.567 | 6 | 7.067 | 0.875 | 8.077 | 9.09 | Sch XXS | 1
1½ | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 1.9 | 48.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.06 | 1.524 | 0.317 | 8.05 | 6 | 7.524 | 0.875 | 8.599 | 10.15 | Sch XXS | 1½
2 | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 2.375 | 60.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.076 | 1.93 | 0.396 | 10.05 | 6 | 7.93 | 0.875 | 9.063 | 11.07 | Sch XXS | 2
3 | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 3.5 | 88.9 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.111 | 2.819 | 0.583 | 14.817 | 6 | 8.819 | 0.875 | 10.079 | 11.13 | Sch 160 | 3
4 | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 4.5 | 114.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.143 | 3.632 | 0.75 | 19.05 | 6 | 9.632 | 0.875 | 11.008 | 11.13 | Sch 120 | 4
6 | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 6.625 | 168.3 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.211 | 5.359 | 1.104 | 28.05 | 6 | 11.359 | 0.875 | 12.982 | 14.27 | Sch 120 | 6
8 | ASTM A106 Gr.B | 175 | 347 | 90 | 1305.4 | 8.625 | 219.1 | 60000 | 35000 | 20000 | 1 | 1 | 0.4 | 0.274 | 6.96 | 1.438 | 36.517 | 6 | 12.96 | 0.875 | 14.811 | 15.09 | Sch 100 | 8
Line Class |  | Design Code |  |  | Base Material |  |  | Flange Rating & Facing |  |  | Corrosion Allowance |  |  | NACE Requirement |  |  | Stress Relief |  |  | Design Temperature (°C) (Min. / Max.) |  | Design Pressure (Bar) (Min. / Max.) |  | Rev
FS00 |  | ASME B31.3 |  |  | Stainless Steel - 316L |  |  | CL.600 - PN 100, R.F. |  |  | 0 (mm) |  |  | - |  |  | - |  |  | - | 175 | - | 62.4 | D02
SERVICE |  | Chemical, Close drain
Size | Material | Temperature |  | Pressuare |  | Outside Diameter | Outside Diameter | Specified Min. Tensile Strength | Specified Min. Yield Strength | Basic Allowable Stress | Quality Factor | Weld Joint Strength Reduction Factor | Temperature Coefficient | Pressure Design Thickness | Pressure Design Thickness | D/6 | D/6 | Corrosion Allowance | Min. Requierd Thickness | Mill Tolerance | Min. Requierd Thickness | Selected Thickness (ASME B36.10M) | Selected Schedule (ASME B36.10M) | Size
NPS (Inch) |  | T (°C) | T (°F) | P (Bar) | P (Psi) | D (Inch) | D (mm) | T (Psi) | Y (Psi) | S (Psi) | E | W | Y | t (Inch) | t (mm) | D/6 (Inch) | D/6 (mm) | c (mm) | tm (mm) | -12.5% | tmil (mm) | ts (mm) | Sch | NPS (Inch)
½ | ASTM A312 Gr.TP316L | 175 | 347 | 62.4 | 905.1 | 0.84 | 21.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.022 | 0.559 | 0.14 | 3.55 | 0 | 0.559 | 0.875 | 0.639 | 2.77 | Sch 40S | ½
¾ | ASTM A312 Gr.TP316L | 175 | 347 | 62.4 | 905.1 | 1.05 | 26.7 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.028 | 0.711 | 0.175 | 4.45 | 0 | 0.711 | 0.875 | 0.813 | 2.87 | Sch 40S | ¾
1 | ASTM A312 Gr.TP316L | 175 | 347 | 62.4 | 905.1 | 1.315 | 33.4 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.035 | 0.889 | 0.219 | 5.567 | 0 | 0.889 | 0.875 | 1.016 | 3.38 | Sch 40S | 1
1½ | ASTM A312 Gr.TP316L | 175 | 347 | 62.4 | 905.1 | 1.9 | 48.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.05 | 1.27 | 0.317 | 8.05 | 0 | 1.27 | 0.875 | 1.451 | 3.68 | Sch 40S | 1½
2 | ASTM A312 Gr.TP316L | 175 | 347 | 62.4 | 905.1 | 2.375 | 60.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.063 | 1.6 | 0.396 | 10.05 | 0 | 1.6 | 0.875 | 1.829 | 3.91 | Sch 40S | 2
3 | ASTM A312 Gr.TP316L | 175 | 347 | 62.4 | 905.1 | 3.5 | 88.9 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.093 | 2.362 | 0.583 | 14.817 | 0 | 2.362 | 0.875 | 2.699 | 5.49 | Sch 40S | 3
4 | ASTM A312 Gr.TP316L | 175 | 347 | 62.4 | 905.1 | 4.5 | 114.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.119 | 3.023 | 0.75 | 19.05 | 0 | 3.023 | 0.875 | 3.455 | 6.02 | Sch 40S | 4
6 | ASTM A312 Gr.TP316L | 175 | 347 | 62.4 | 905.1 | 6.625 | 168.3 | 70000 | 25000 | 16700 | 1 | 1 | 0.4 | 0.176 | 4.47 | 1.104 | 28.05 | 0 | 4.47 | 0.875 | 5.109 | 7.11 | Sch 40S | 6
D02
D02
D02
D02
D02
D02
D02
D02