## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0003_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1093 |  |  | Transmital Date: 19/Jun/2022
Document Title: Mechanical Data Sheets For 1st Stage Gas Air Coolers |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-ME-TR-1093 |  |  | Transmital Date: 19/Jun/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-ME-DT-0003_D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بند 3 نامه شماره 00/2294/372926 اصلاح نشده است و اطلاعات مربوط به تبادل حرارت با اسناد پایه مغایرت دارد. |  | 01/2294/183492 | 1401/05/27 | اطلاعات مربوط به تبادل حرارتی با توجه به تغییر کامپوزیشن و دبی جریان های ورودی به ایستگاه جدید تقویت فشار بینک بروزرسانی شده است.
2 | محاسبات مربوط به MDMT ارائه گردد. |  | 01/2294/183492 | 1401/05/27 | محاسبات MDMT در مدرک Calculation Note For Depressurizing (Min. Design Temperature ) به شماره مدرک BK-GCS-PEDCO-120-PR-CN-0007 ارائه شده است.
3 | نوع Fin در مدرک Embedded قید گردد. |  | 01/2294/183492 | 1401/05/27 | با توجه به دمای طراحی نیازی به نوع فین Embedded نیست و می توان از نوع فین Extruded استفاده کرد.
4 | تست HIC/SSC برای متریال انجام شود. |  | 01/2294/183492 | 1401/05/27 | تست های مذکور بر روی متریال S.S 316L موضوعیت ندارد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature | H.Naserizadeh |  |  | Clarified By: H.Adineh | Signature
| Date: |  |  |  |  | Date: 10/4/2022