## Reply Sheet
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-CV-DW-0004 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0059 |  |  | Transmital Date: 22-AUG-2021
Document Title: Standard Drawing For Electrical Cable Trench |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-CV-T-0059 |  |  | Transmital Date: 22-AUG-2021
[5 empty] | CRS No:NISOC-CRS-BK-GNRAL-PEDCO-000-CV-DW-0004-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | الزامات بخش برق می بایست در این مدرک رعایت شده باشد، لذا وجود هرگونه مغایرت با استانداردهای بخش مذکور بر عهده ی پیمانکار خواهد بود. |  | 1400-2294-173204 | 1400/06/03 | مدرک دستگردانی داخلی شده است و با استانداردهای برق و ابزار دقیق همخوانی دارد
2 | جداول مربوط به اندازه ی ارتفاع در مدارک ترسیم شود. |  | 1400-2294-173204 | 1400/06/03 | با توجه به الزامات بخش برق و ابزار دقیق در هر بخش از پروژه در مدرک UG ارتفاع و تیپیکالهای مرتبط ارائه خواهد گردید
3 | تراکم خاک بستر در ترسیمات لحاظ گردد. |  | 1400-2294-173204 | 1400/06/03 | با توجه به ابعاد و عمق ترنچ امکان متراکم کردن خاک با غاطک میسر نیست و بنابراین با توجه به طبیعی بودن خاک در این عمق پس از تخلیه خاک دستی متراکم کردن خاک در حد اتو کشی انجام خواهد شد
4 | نوع سیمان می بایست بر اساس گزارش مطالعات ژئوتکنیک در نقشه ها درج شود. |  | 1400-2294-173204 | 1400/06/03 | اعمال شد
5 | Note 11 ناقص است، لذا اصلاح گردد. |  | 1400-2294-173204 | 1400/06/03 | اعمال شد
6 | ارائه ی ترسیم تمامی نقشه ها در صفحه ی مدل صحیح نیست، لذا هر صفحه در Layout مجزا تدوین گردد. |  | 1400-2294-173204 | 1400/06/03 | اعمال شد
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: