| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| STRUCTURAL CALCULATION NOTE FOR CONTROL BUILDING نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| D00 | OCT. 2022 | IFC | R.Berlouie | M.Fakharian | M.Mehrshad |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | CLIENT Approval |
| Class:2 |  | CLIENT Doc. Number:F0Z-709118 |  |  |  |  |
| Status: | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X |  |  |  |  |  | 66 |  |  |  |  |  |
| 2 | X |  |  |  |  |  | 67 |  |  |  |  |  |
| 3 | X |  |  |  |  |  | 68 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 69 |  |  |  |  |  |
| 5 | X |  |  |  |  |  | 70 |  |  |  |  |  |
| 6 | X |  |  |  |  |  | 71 |  |  |  |  |  |
| 7 | X |  |  |  |  |  | 72 |  |  |  |  |  |
| 8 | X |  |  |  |  |  | 73 |  |  |  |  |  |
| 9 | X |  |  |  |  |  | 74 |  |  |  |  |  |
| 10 | X |  |  |  |  |  | 75 |  |  |  |  |  |
| 11 | X |  |  |  |  |  | 76 |  |  |  |  |  |
| 12 | X |  |  |  |  |  | 77 |  |  |  |  |  |
| 13 | X |  |  |  |  |  | 78 |  |  |  |  |  |
| 14 | X |  |  |  |  |  | 79 |  |  |  |  |  |
| 15 | X |  |  |  |  |  | 80 |  |  |  |  |  |
| 16 | X |  |  |  |  |  | 81 |  |  |  |  |  |
| 17 | X |  |  |  |  |  | 82 |  |  |  |  |  |
| 18 | X |  |  |  |  |  | 83 |  |  |  |  |  |
| 19 | X |  |  |  |  |  | 84 |  |  |  |  |  |
| 20 | X |  |  |  |  |  | 85 |  |  |  |  |  |
| 21 | X |  |  |  |  |  | 86 |  |  |  |  |  |
| 22 | X |  |  |  |  |  | 87 |  |  |  |  |  |
| 23 | X |  |  |  |  |  | 88 |  |  |  |  |  |
| 24 | X |  |  |  |  |  | 89 |  |  |  |  |  |
| 25 | X |  |  |  |  |  | 90 |  |  |  |  |  |
| 26 | X |  |  |  |  |  | 91 |  |  |  |  |  |
| 27 | X |  |  |  |  |  | 92 |  |  |  |  |  |
| 28 | X |  |  |  |  |  | 93 |  |  |  |  |  |
| 29 | X |  |  |  |  |  | 94 |  |  |  |  |  |
| 30 | X |  |  |  |  |  | 95 |  |  |  |  |  |
| 31 | X |  |  |  |  |  | 96 |  |  |  |  |  |
| 32 | X |  |  |  |  |  | 97 |  |  |  |  |  |
| 33 | X |  |  |  |  |  | 98 |  |  |  |  |  |
| 34 | X |  |  |  |  |  | 99 |  |  |  |  |  |
| 35 | X |  |  |  |  |  | 100 |  |  |  |  |  |
| 36 | X |  |  |  |  |  | 101 |  |  |  |  |  |
| 37 | X |  |  |  |  |  | 102 |  |  |  |  |  |
| 38 | X |  |  |  |  |  | 103 |  |  |  |  |  |
| 39 | X |  |  |  |  |  | 104 |  |  |  |  |  |
| 40 | X |  |  |  |  |  | 105 |  |  |  |  |  |
| 41 | X |  |  |  |  |  | 106 |  |  |  |  |  |
| 42 | X |  |  |  |  |  | 107 |  |  |  |  |  |
| 43 | X |  |  |  |  |  | 108 |  |  |  |  |  |
| 44 | X |  |  |  |  |  | 109 |  |  |  |  |  |
| 45 | X |  |  |  |  |  | 110 |  |  |  |  |  |
| 46 | X |  |  |  |  |  | 111 |  |  |  |  |  |
| 47 | X |  |  |  |  |  | 112 |  |  |  |  |  |
| 48 | X |  |  |  |  |  | 113 |  |  |  |  |  |
| 49 | X |  |  |  |  |  | 114 |  |  |  |  |  |
| 50 | X |  |  |  |  |  | 115 |  |  |  |  |  |
| 51 | X |  |  |  |  |  | 116 |  |  |  |  |  |
| 52 | X |  |  |  |  |  | 117 |  |  |  |  |  |
| 53 | X |  |  |  |  |  | 118 |  |  |  |  |  |
| 54 | X |  |  |  |  |  | 119 |  |  |  |  |  |
| 55 | X |  |  |  |  |  | 120 |  |  |  |  |  |
| 56 | X |  |  |  |  |  | 121 |  |  |  |  |  |
| 57 | X |  |  |  |  |  | 122 |  |  |  |  |  |
| 58 | X |  |  |  |  |  | 123 |  |  |  |  |  |
| 59 | X |  |  |  |  |  | 124 |  |  |  |  |  |
| 60 | X |  |  |  |  |  | 125 |  |  |  |  |  |
| 61 |  |  |  |  |  |  | 126 |  |  |  |  |  |
| 62 |  |  |  |  |  |  | 127 |  |  |  |  |  |
| 63 |  |  |  |  |  |  | 128 |  |  |  |  |  |
| 64 |  |  |  |  |  |  | 129 |  |  |  |  |  |
| 65 |  |  |  |  |  |  | 130 |  |  |  |  |  |

CONTENTS

1.0	INTRODUCTION	4

2.0	Scope	5

3.0	NORMATIVE REFERENCES	5

-	Local Codes and Standards	5

-	International Codes and Standards	5

-	The Project Documents	5

-	ENVIRONMENTAL DATA	5

-	Order of Precedence	5

4.0	DESIGN INFORMATION	6

-	Structure LOCATION	6

-	ARCHITECTURAL PLANS	7

5.0	material properties	8

-	reinforced concrete	8

-	cement	9

-	STIFFNESS MODIFICATION	9

6.0	design loads	10

-	general	10

-	DEAD LOAD	12

-	LIVE LOAD	14

-	HORIZONTAL SEISMIC LOAD	15

-	Redundancy Factor ρ	17

-	BLAST LOAD	17

7.0	Structural design	22

-	dynamic increase factor	22

-	LOAD COMBINATIONS FOR REINFORCED CONCRETE STRUCTURE	23

-	CONTROL BUILDING design	32

-	COLUMN design	32

-	BEAM design	35

-	WALL design	41

-	slab design	49

-	settlement of the foundation	52

-	Foundation design for resultant forces	53

-	DRIFT CONTROL	57

-	frame control for 25% earth quake force	58

-	frame control for (5/6) BEAM/COLUMN CAPACITY RATIOS	59

-	JOINT SHEAR CAPACITY RATIOS	60

- INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

As a part of the Project, a New Gas Compressor Station (adjacent to existing Binak GCS) shall be constructed to gather of 15 MMSCFD (approx.) associated gases and compress & tra	nsfer them to Siahmakan GIS.

GENERAL DEFINITION

The following terms shall be used in this document.

| CLIENT: | National Iranian South Oilfields Company (NISOC) |
| --- | --- |
| PROJECT: | Binak Oilfield Development – Surface Fcilities; New Gas Compressor Station |
| EPD/EPC CONTRACTOR (GC): | Petro Iran Development Company (PEDCO) |
| EPC CONTRACTOR: | Joint Venture of : Hirgan Energy – Design & Inspection (D&I) Companies |
| VENDOR: | The firm or person who will fabricate the equipment or material. |
| EXECUTOR: | Executor is the party which carries out all or part of construction and/or commissioning for the project. |
| THIRD PARTY INSPECTOR (TPI): | The firm appointed by EPD/EPC CONTRACTOR (GC) and approved by CLIENT (in writing) for the inspection of goods. |
| SHALL: | Is used where a provision is mandatory. |
| SHOULD: | Is used where a provision is advisory only. |
| WILL: | Is normally used in connection with the action by CLIENT rather than by an EPC/EPD CONTRACTOR, supplier or VENDOR. |
| MAY: | Is used where a provision is completely discretionary. |

- Scope

This document covers minimum necessary requirements for the design, selection, manufacture and inspection.

- NORMATIVE REFERENCES

## Local Codes and Standards

- IPS-E-PR-905                  	Engineering Standard for Process Design of Dryers

- IPS-E-PR-330	Engineering Standard for Process Design of Compressed Air Systems

## International Codes and Standards

- ASTM	American Society for Testing Materials Relevant Parts

- API 610	Centrifugal Pumps for General Refinery Service, 10th Edition

- ISO 15156	Petroleum and Natural Gas Industries. Materials for use in H2S Containing Environments in Oil and Gas Production

## The Project Documents

- --------------------------	Process Basis of Design

- --------------------------	Process Design Criteria

## ENVIRONMENTAL DATA

Refer to "Process Basis of Design; Doc. No. -----------------------".

## Order of Precedence

In case of any conflict between the contents of this document or any discrepancy between this document and other project documents or reference standards, this issue must be reported to the CLIENT. The final decision in this situation will be made by CLIENT.

- DESIGN INFORMATION

## Structure LOCATION

The Control Building is located in Binak oilfield.

Figure 1- Project Location

## ARCHITECTURAL PLANS

Figure 2 – PLAN OF CONTROL BUILDING

Figure 3 – SECTION A-A

- material properties

## reinforced concrete

Concrete shall generally conform to the specification for concrete work report No:BK-GNRAL-PEDCO-000-ST-SP-001- The following properties of concrete are used.

Lean concrete: f’c =150 kg/cm2

Cast in place concrete: f’c =350 kg/cm2

Where f'c is the minimum compressive characteristic strength of a cylinder specimen at 28 days.

Young Modulus of concrete: Ec=15100f'c  kg/cm2

Poisson's Ratio: ν = 0.2

Unit weight of reinforced concrete: 2500 kg/m3

## cement

Cement shall conform to the following specifications for Portland cement:

a) "Standard Specification for Portland Cement" (ASTM C 150). [5.1, 6.1.1]

Cement type shall be considered according to geotechnical investigation report.

Cement used in the work shall correspond to that on which selection of concrete proportions was based. [5.1, 6.1.2]

Fly Ash or other pozzolans shall conform to  ASTM  C  618   "Standard Specification for Coal Fly Ash and Raw or Calcined Natural Pozzolan for Use in Concrete" For more information about other kinds of pozzolans see Iranian national concrete code Publication No.-120 of management and planning organization part 3-6- 4-2. [5.1, 6.1.3]

## STIFFNESS MODIFICATION

For analysis of concrete structure, the following modifications for flexural stiffness of elements are considered.

Columns………………………………..0.7Ig

Beams………………………………….0.35Ig

Wall (Cracked)……………..………….0.35Ig

Slabs………………………….……….0.25Ig

- design loads

## general

Considered loads are as follows.

- Dead Load.

- Live Load.

- Wall Load.

- Earthquake Load.

- Blast load.

- Thermal Load.

Table 1- Define Load Patterns

| Define Load Patterns |  |  |
| --- | --- | --- |
| Load Pattern Name | Type | CONTROL BUILDING |
| DEAD | Dead |  |
| Wall | Dead |  |
| Live | Live |  |
| EX | Quake |  |
| EY | Quake |  |
| BLAST1 | Live |  |
| BLAST2 | Live |  |
| BLAST3 | Live |  |
| BLAST4 | Live |  |
| Th+20 | Temperature |  |
| Th-20 | Temperature |  |

## DEAD LOAD

Dead Load is considered as the weight of materials forming a permanent part of the structure plant. The weight of materials of construction incorporated into the building, including but not limited to walls, floors, roofs, ceilings, stairways, built-in partitions, finishes, cladding and other similarly incorporated architectural and structural items, and the weight of fixed service equipment, such as plumbing stacks and risers, electrical feeders, heating, ventilating and air-conditioning systems.

Specific weight of materials which will be used is based on Iranian National Building Code, Part 6, where applicable. Other weights are in accordance with the specifications and/or drawings of vendors and manufacturers.

Here is the calculation of design dead load for floors, walls including External and Internal walls.

Table 2- Calculation of Roof Dead load

| NO. | Description | specific weight (kg/m3) | thickness (cm) | kg/m2 |
| --- | --- | --- | --- | --- |
| 1 | ceramic | 2400 | 2.0 | 48 |
| 2 | cement mortar | 2100 | 2.0 | 42 |
| 3 | 2 layer bitumen & gunny | ------ | ------- | 15.0 |
| 4 | cement mortar | 2100 | 2.5 | 52.5 |
| 5 | Expanded aggregate | 850 | 10 | 85 |
| 6 | Slab 20 cm | Calculated by Sap | ----- | ----- |
| 7 | Thermal insulation of polystyrene | 100 | 10 | 10 |
| 8 | Plaster and soil mortar | 1600 | 2 | 32 |
| 9 | Gypsum Plaster | 1300 | 1 | 13 |
| 10 | Suspended ceiling | --- | --- | 50 |
|  | SUM |  |  | 347.5 |
|  | Applied to model |  |  | 350 |

Table 3- Wall Dead load

| NO. | Description | specific weight (kg/m3) | thickness (cm) | kg/m2 |
| --- | --- | --- | --- | --- |
| 1 | PRESSED BRICK | 1700 | 20 | 340 |
| 2 | GYPSUM PLASTER | 1300 | 4 | 52 |
|  |  | SUM |  | 392 |
|  |  | Applied to model |  | 400 |

## LIVE LOAD

Live Load is defined as the weight of all movable loads, including partition walls, personnel, tools, miscellaneous equipment and temporarily stored materials.

Generally where applicable, the live loads shall be in accordance with Iranian National Building Code, Part 6. The Live Loads is generally considered as uniformly distributed over the horizontal projection of the loaded areas, except for the loads with a concentrated nature.

The live load has been considered according to the following table.

Table 4- Live load on structure.

| NO. | Level | kg/m2 |
| --- | --- | --- |
| 1 | Roof | 150 |
| 2 | Administrative parts | 250 |
| 3 | Other parts | 500 |

## HORIZONTAL SEISMIC LOAD

According to Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition) the structure shall be designed for earthquake load in two orthogonal directions.

Base level is defined as the level below which the structure does not move relative to the ground during an earthquake. For this structure base level is top of the deck level.

Basic parameters which are used in calculation of earthquake forces are presented below.

Following formula is used for calculations according to Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition)

Vu=SaRuIW

In which:

Vu: Basic shear

Sa: mapped spectral response acceleration parameter (𝑔)

I: Importance factor of structure

Ru: Structural system factor

W= effective seismic weight of the structure, including dead loads and other loads, calculated from base level.

Table 5- Basic parameters used for earthquake loads calculation

| Height of the structure from the base level (m) | 5.55 |
| --- | --- |
| Importance factor, I | 1.5 |
| Structural system | Special bending frame with special reinforced concrete shear wall |
| Soil type | II |
| A | 0.30 |
| Ru | 7 |
| Ct | 0.05 |
| x | 0.75 |
| Tx&Y (calculation) =Ct.Hx | 0.18 |
| Tx (analysis) – mode 1 | 0.05 |
| Ty (analysis) – mode 3 | 0.05 |
| Tx select for design= Tanalysis | 0.05 |
| TY select for design= Tanalysis | 0.05 |
| B=B1*N & N=1 | 2.5 |
| Sax and Say | 0.75 |
| Kx & Ky →T<0.5 | 1 |
| Cmin=0.044SDSI | 0.165 |
| Cx& Cy=SaxRuI | 0.163 |
| Cx*ρ & Cy*ρ-(ρ=1.0) | 0.165 |
| Service level earthquake =1/6.A.B.I | 0.187 |

## Redundancy Factor ρ

According to Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition Paragraph 4-6) - ρ =1.0

## BLAST LOAD

According to Appendix IC of IPS-E-CE-500 (ADDITIONAL REQUIREMENTS FOR BLAST RESISTANT BUILDINGS AND STRUCTURES), the blast pressure of exterior walls and roof are as below:

Table 6- Blast Load

| Item | Pr | P0 | t0 |
| --- | --- | --- | --- |
|  | Kpa | Kpa | msec |
| Front Wall | 172 |  | 20 |
| Back Wall |  | 70 | 20 |
| Right Wall | 172 |  | 20 |
| Left Wall | 172 |  | 20 |
| Roof |  | 70 | 20 |

Figure 4- Mode 1 in Blast Load

Figure 5- Mode 2 in Blast Load

Figure 6- Mode 3 in Blast Load

Figure 7- Mode 4 in Blast Load

- Structural design

## dynamic increase factor

fdy=SIF*DIF*fy

fdu=SIF*DIF*fu

f'dc=SIF*DIF*f'c

Table 7- dynamic increase factor

| Material | Concrete |  | Rebar |  | St37 |  | St52 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | SIF | DIF | SIF | DIF | SIF | DIF | SIF | DIF |
| fdy | - | - | 1.15 | 1.20 | 1.15 | 1.25 | 1.15 | 1.2 |
| fdu | - | - | 1.15 | 1.05 | 1.15 | 1.1 | 1.15 | 1.05 |
| f'dc | 1.1 | 1.15 | - | - | - | - | - | - |

## LOAD COMBINATIONS FOR REINFORCED CONCRETE STRUCTURE

These load combinations will be considered according to the Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition Design)

Table 8- Load combination for design (EARTH QUAKE)

Table 9- Load combination for design (EARTH QUAKE)

Table 10- Load combination for Soil control

Table 11- Load combination for Soil control

Table 12- Load combination for Soil control

Table 13- Load combination for Soil control

Table 14- Load combination for design (BLAST LOAD)

Table 15- Load combination for design (THERMAL LOAD)

Figure 8- 3D MODEL OF CAPACITOR BANK

Figure 9- 3D MODEL OF CAPACITOR BANK

## CONTROL BUILDING design

## COLUMN design

Figure 10- COLUMN DESIGN (EARTH QUAKE)

Figure 11- COLUMN DESIGN (BLAST LOAD)

Figure 12- COLUMN DESIGN (THERMAL LOAD)

## BEAM design

Figure 13- BEAM DESIGN (EARTH QUAKE)

`

Figure 14- BEAM DESIGN FOR TORSION (EARTH QUAKE)

Figure 15- BEAM DESIGN (BLAST LOAD)

Figure 16- BEAM DESIGN FOR TORSION (BLAST LOAD)

Figure 17- BEAM DESIGN (THERMAL LOAD)

Figure 18- BEAM DESIGN FOR TORSION (THERMAL LOAD)

## WALL design

Figure 19- MAX M11(+) & (-) ton-m) - (EARTH QUAKE)

Figure 20- MAX M22(+) & (-) ton-m) - (EARTH QUAKE)

Figure 21- MAX M11(+) & (-) (ton-m) - (BLAST)

Figure 22- MAX M22(+) & (-) (ton-m) - (BLAST)

Figure 23- MAX M11(+) & (-) (ton-m) - (THERMAL)

Figure 24- MAX M22(+) & (-) (ton-m) - (THERMAL)

Table 16- WALL RESULTANT FORCES

| RESULTANT FORCES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| LOAD | M11(ton-m) |  | M22(ton-m) |  | V (ton) |
|  | MAX (+) | MAX (-) | MAX (+) | MAX (-) | MAX |
| Earth Quake | 0.30 | 0.30 | 1.5 | 2 | 3 |
| BLAST | 11.0 | 16.0 | 14.0 | 16.0 | 18 |
| Thermal | -1 | 1 | -2.20 | 1 | 1.5 |
| Select for design | 11.0 | 16.0 | 14.0 | 16.0 | 18.0 |

able 17- WALL DESIGN

Table 18- WALL DESIGN

Table 19- WALL ROTATION ANGLE

| WALL ROTATION ANGLE-(UFC 3-340) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Wall | Load | Xm (cm) | H (cm) | θ°max | Control |
| Wall “a” | Blast-1 | 1.54 | 530 | 0.33 | O.K |
| Wall “b” | Blast-2 | 1.45 | 530 | 0.30 | O.K |
| Wall “c” | Blast-3 | 1.40 | 630 | 0.22 | O.K |
| Wall ”d” | Blast-4 | 1.55 | 630 | 0.28 | O.K |

Vu=18.0 ton

Vn=Vc+Vs

Vc=f'c6bwd=44.261000*240=265932.32N=26.59 ton

Vu>0.5Vc=13.295

USE∅8@300x300mm

Vs=Av.fy.ds=50.24*552*240300=22185.98*3=66557.95 N=6.65 ton

Vn=26.59+6.65=33.24 ton.>18 ton. →O.K

## slab design

| MAX M11(+) | MAX M11(-) |
| --- | --- |
| MAX M22(+) | MAX M22(-) |

Figure 25- MAX SLAB RESULTANT FORCES

Table 20- SLAB RESULTANT FORCES

| RESULTANT FORCES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| LOAD | M11(ton-m) |  | M22(ton-m) |  | V (ton) |
|  | MAX (+) | MAX (-) | MAX (+) | MAX (-) | MAX |
| Blast load | 2.0 | 4.5 | 2.5 | 5.0 | 5.0 |
| Earth Quake | 0.7 | 1.5 | 0.5 | 0.7 | 1.2 |
| Thermal | 0.5 | 0.7 | 0.7 | 0.8 | 1.5 |
| Select for design | 2 | 4.5 | 2.5 | 5.0 | 5 |

Table 21- SLAB DESIGN

Table 22- SLAB ROTATION ANGLE

| WALL ROTATION ANGLE-(UFC 3-340) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SLAB | Load | Xm (cm) | H (cm) | θ°max | Control |
| ROOF | Blast | 2.93 | 530 | 0.63 | O.K |

Vu=5.0 ton

Vn=Vc+Vs

Vc=f'c6bwd=44.261000*150=166207.7N=16.62 ton

Vu<0.5Vc=8.31→O.K

Minimum Shear Reinforcement-USE∅8@300x300mm

## settlement of the foundation

Table 23- FOUNDATION DISPLACEMENTS-EARTH QUAKE LOAD-cm

Table 24- FOUNDATION DISPLACEMENTS- BLAST LOAD -cm

The maximum settlement of the foundation =2.4 cm <5cm – O.K

## Foundation design for resultant forces

| M11- MAX (-) | M11- MAX (+) |
| --- | --- |
| M22- MAX (-) | M22- MAX (+) |

Figure 26- MAX FOUNDATION RESULTANT FORCES - (ton-m) (EARTH QUAKE)

| M11- MAX (-) | M11- MAX (+) |
| --- | --- |
| M22- MAX (-) | M22- MAX (+) |

Figure 27- MAX FOUNDATION RESULTANT FORCES - (ton-m) (BLAST LOAD)

Table 25- FOUNDATION RESULTANT FORCES

| RESULTANT FORCES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| LOAD | M11(ton-m) |  | M22(ton-m) |  | V (ton) |
|  | MAX (+) | MAX (-) | MAX (+) | MAX (-) | MAX |
| Blast load | 30&13 | 30&18 | 25&10 | 35&16 | 40&20 |
| Earth Quake | 20 &10 | 11 | 7 | 11 | 18 |
| Select for design | 30&13 | 30&18 | 25&10 | 35&16 | 40&20 |

Table 26- FOUNDATION DESIGN

Table 27- FOUNDATION DESIGN

Vu=40.0 ton

Vn=Vc+Vs

Vc=f'c6bwd=44.261000*525=581726.95N=58.17 ton

Vu>0.5Vc=29.08ton

USE∅8@400x400mm

Vs=Av.fy.ds=50.24*552*525400=36398.88*2=72797.76 N=7.2 ton

Vn=58.17+7.2=65.37 ton.>40.0 ton. →O.K

## DRIFT CONTROL

The design lateral displacement (nonlinear) at level 𝑥 shall be calculated from Equation below according to Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition).

δx=CdδxeI

𝛿𝑥𝑒= elastic lateral displacement at level 𝑥, according to lateral load distribution from Equivalent Lateral Load Procedure or Modal Response Spectrum Analysis.

Stiffness modification for drift calculation:

Flat slabs & plates = 0.25 Ig

Beams = 0.35 Ig

Columns =0.7 Ig

Wall =0.35 Ig

Table 28- Drift Control (cm)

∆ex&∆ey≪0.011.5=0.0066→O.K

## frame control for 25% earth quake force

Figure 28- COLUMN DESIGN (25%EARTH QUAKE)

Figure 29- BEAM DESIGN (25% EARTH QUAKE)

## frame control for (5/6) BEAM/COLUMN CAPACITY RATIOS

Figure 30- (5/6) BEAM/COLUMN CAPACITY RATIOS

## JOINT SHEAR CAPACITY RATIOS

Figure 31- JOINT SHEAR CAPACITY RATIOS