## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DT-0010_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0906 |  |  | Transmital Date: 8 May 2022
Document Title: Data Sheets For ON/OFF & Shutdown Valves |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-0906 |  |  | Transmital Date: 8 May 2022
[5 empty] | CRS No: NISOIC-CRS-BK-GCS-PEDCO-120-IN-DT-0010_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | لیست مدارک مرجع لازم ذکر گردد ازز جمله مدارک ذیل: Instrument & Control System Design Criteria Specification For Hazardous Area Classification Specification For On-off /Shut Down Valves(ESDV/MOV) |  | 01/2294/82869 | 1401/03/09 | مدرک مطابق نظر کارفرمای محترم اصلاح گردید.
2 | کلاس کاری فلنج تجهیزات به اشتباه درج شده است. |  | 01/2294/82869 | 1401/03/09 | مدرک اصلاح گردید.
3 | برای این شیرآلات Trim No. 12 در نظر گرفته شود. |  | 01/2294/82869 | 1401/03/09 | جنسTrim شیرها مطابق مدرک Piping Material Specification اصلاح و بروز رسانی گردید، لازم به ذکر است Trim No. 12 برای شیرهای Globe , Check,... استفاده شده است و برای Ball valve ها بیان نشده است.
4 | داده های محیطی می بایست براساس آخرین ویرایش مدرک Process Design Basis مد نظر قرار گیرد. |  | 01/2294/82869 | 1401/03/09 | مدرک اصلاح گردید.
5 | عبارتShutdown در عنوان و سربرگ مدرک اصلاح گردد. |  | 01/2294/82869 | 1401/03/09 | مدرک اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 5/21/2022 |  |  |  |  | Date: