## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DT-0009_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0967 |  |  | Transmital Date: 17 May 2022
Document Title: Data Sheets For Pressure & Safety Relief Valves |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-0967 |  |  | Transmital Date: 17 May 2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-IN-DT-0009_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument Comments
1 | ليست مدارك مرجع در ديتا شيت اضافه گردد. |  | BK-SUR-ENG-INS-01-04510 | 2022-06-01 | اعمال گردید.
2 | در قسمت PURCHASE عبارت will be finalized later اضافه گردد. |  | BK-SUR-ENG-INS-01-04510 | 2022-06-01 | اعمال گردید.
3 | متريال spring مطابق با مدرك specification for PSV در نظر گرفته شود. |  | BK-SUR-ENG-INS-01-04510 | 2022-06-01 | مطابق با آیتم 5.7 مدرک SPECIFICATION FOR PRESSURE SAFETY VALVES(PSV)، متریال spring و valve body می بایست یکسان باشد.
4 | با توجه به مغايرت بين اطلاعات خط در P&ID و ديتاشيت، اطلاعات مربوط به متريال بر اساس آخرين مستندات مجددا مورد بازنگري قرار گيرد. |  | BK-SUR-ENG-INS-01-04510 | 2022-06-01 | بررسی و بازنگری گردید.
5 | تست ها مانند Hydro test و seat leakage test در نظر گرفته شود. |  | BK-SUR-ENG-INS-01-04510 | 2022-06-01 | اعمال گردید.
6 | رويژن P&ID مشخص شود. |  | BK-SUR-ENG-INS-01-04510 | 2022-06-01 | اعمال گردید.
Process Comments
7 | با توجه به وجود نقطه نظرات اساسي بر مدرك محاسبات شيرهاي ايمني بخش فرآيند (همچون عدم درنظر گرفتن سناريوهاي محتمل، اشكال در محاسبات انجام شده و...) ، اين مدرك به لحاظ فرآيندي تا رسيدن به حداقل كيفيت مدرك پيشنياز (محاسبات شيرهاي ايمني) قابل بررسي نمي باشد. |  | BK-SUR-ENG-INS-01-04510 | 2022-06-01 | این مدرک با گروه پروسس idc گردید و آخرین نقطه نظرات پروسس بر روی این مدرک اعمال گردید.
Piping Comments
8 | نقطه نظرات پايپينگ در فايل پيوست آمده است. |  | BK-SUR-ENG-INS-01-04510 | 2022-06-01 | 1. شماره ی P&ID اصلاح گردید. 2. مطابق با P&ID ، کلاس ورودی و خروجی و ریتینگ و سایز تصحیح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date:31 May 2022 |  |  |  |  | Date: