## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-PY-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0947 |  |  | Transmital Date: 14-May-2022
Document Title: Area Lighting & Small Power Layout of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0947 |  |  | Transmital Date: 14-May-2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-EL-PY-0003_D00 (1) |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | یک پریز تکفاز 16 آمپر مجاور پریز سه فاز جوشکاری با مدار جداگانه در نظر گرفته شود |  | 1401-2294-92409 | 1401-03-17 | پریز 16 آمپر تکفاز مجاور سوکت سه فاز جوشکاری که از این سوکت تغذیه می کند در نظر گرفته شد.
2 | یک پریز تکفاز 16 آمپر در محوطه ترانس در نظر گرفته شود. |  | 1401-2294-92409 | 1401-03-17 | پریز تکفار در اتاق ترانس وجود دارد که در نقشه روشنایی مربوطه به شماره " BK-SSGRL-PEDCO-110-EL-PY-0004" نشان داده شده است.
3 | پس از تأیید مدارک محاسبات روشنایی، چیدمان نورافکرنهای سایت بازنگری گردد. |  | 1401-2294-92409 | 1401-03-17 | آخرین ویرایش مدرک محاسباتی محوطه سرچاهی با شماره ترنسمیتال 1496 برای آن کارفرمای محترم ارسال گردید
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 23-May-22 |  |  |  |  | Date: