## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-PY-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0947 |  |  | Transmital Date: 14-May-2022
Document Title: Area Lighting & Small Power Layout of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0947 |  |  | Transmital Date: 14-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-PY-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised and issued as IFA after finalizing or minor comments on following documents: -Calculation Note For Lighting System of Well Pads Area -Plot plan Drawing -Hazardous area classification layout |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | اعمال گردید.
2 | According to NO. of outdoor area lighting panel feeders, It is recommended to area lighting feeders be supplied from security building lighting panel. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | به علت گستردگی سایت و فاصله از ساختمان نگهبانی تا پایه های روشنایی، تابلو WELL XX-DP03 تغذیه شونده از سوئیچگیر به صورت مجزا در نظر گرفته شده است.
3 | Lighting fixture, outdoor installation shall be considered IP65. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | مطابق با استاندارد پروژه روشنایی بیرونی بایستی IP55 می باشد.
4 | Typical installation detail for each lighting equipment shall be added and specified base on "Typical Installation Details & Notes For Lighting System". |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | با توجه به اینکه در این مدرک تنها یک مدل چراغ روشنایی وجود دارد لذا نحوه قرارگیری و نصب نمایش داده شده است. همچنین نحوه نصب سوکت بر روی پایه نیز نشان داده شده است.
5 | It shall be checked that welding sockets in layout needs to JB or not base on related incoming cable and cable between them. Meanwhile IP for WS shall be specified, too. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | JB لحاظ گردید.
6 | Hazardous area classification layout shall be added as reference documents. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | اعمال گردید.
7 | Complementary comments will be submitted after received revised document. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | در صورت وجود کامنت متعاقبا بررسی خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 23-May-22 |  |  |  |  | Date: