## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-EL-SL-0001_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1026 |  |  | Transmital Date: 31-May-2022
Document Title: Single line diagram for expansion of upstream lv switchgear in siahmakan gas injection |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1026 |  |  | Transmital Date: 31-May-2022
[5 empty] | CRS No: NISOC-CRS-BK-PPL-PEDCO-320-EL-SL-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | شماره فیدر اختصاص یافته به ترانس انتهای مسیر در واحد سیاهمکان (فیدر 63 آمپر L11 از سلول شماره 5) بر اساس سوابق بنامه (نامه 80877) در نقشه قید گردد. |  | 1401-2294-111571 | 1401-03-31 | اعمال گردید.
2 | در این مدرک نقشه سیستم موجود نمایش داده شده و فیدر مربوط به سیستم حفاظت کاتدی در آن ترسیم شود. به پیوست فایل الکترونیکی مربوط به کلیدخانه موجود واحد تزریق گاز سیاهمکان ارسال می گردد. |  | 1401-2294-111571 | 1401-03-31 | مطابق با نقشه دریافتی از آن کارفرمای محترم، این فیدر به صورت کشویی بوده و تنها یک عدد کلید MCCB 3 پل دارد . همین موارد بر روی نقشه در نظر گرفته شد.
3 | جهت حفاظت کابل حفاظت 50G لحاظ گردد. |  | 1401-2294-111571 | 1401-03-31 | مطابق با توضیحات کامنت 2 و با توجه به اینکه این فیدر L11 در اختیار پیمانکار قرار می گیرد، امکان قراردادن حفاظت 50G وجود ندارد. چراکه در داخل تابلو این تجهیز وجود ندارد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 14-Jun-2022 |  |  |  |  | Date: