## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-EL-SL-0001_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1026 |  |  | Transmital Date: 31-May-2022
Document Title: Single line diagram for expansion of upstream lv switchgear in siahmakan gas injection |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1026 |  |  | Transmital Date: 31-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-PPL-PEDCO-320-EL-SL-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | It shall be revised after finalizing or minor comments on electrical load list in siahmakan gas injection. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | مدرک محاسباتی حفاظت کاتودیک در دست تولید می باشد. بعد از نهایی شدن آن مدرک لیست بار نیز به روز شده و جهت تأیید ارسال می گردد.
2 | It shall be clearly mentioned and shown that required power for feeding cathodic protection trans/rectifier will be supply from EXISTING spare LV feeder of existing LV switchgear. This feeder picture is attached. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | طی بازدید به عمل آمده از سایت سیاهمکان و همچنین دیاگرام تک خطی دریافت شده از کارفرمای محترم طی نامه شماره 111571، فیدر 63 آمپر موجود برای تغذیه حفاظت کاتودیک اختصاص داده شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 14-Jun-2022 |  |  |  |  | Date: