## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-SL-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0947 |  |  | Transmital Date: 14-May-2022
Document Title: Single Line Diagram For LV Power Distribution Panel of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0947 |  |  | Transmital Date: 14-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-SL-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This documents shall be revised and issued as IFA after finalizing or minor comments on lighting and small power layout. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | این مدرک مطابق با آخرین ویرایش مدرک جانمایی روشنایی اصلاح گردید و در صورت هر گونه تغییر، مدارک ویرایش خواهد شد.
2 | According to NO. of outdoor area lighting panel feeders, It is recommended to area lighting feeders be supplied from security building lighting panel. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | به علت گستردگی سایت و فاصله از ساختمان نگهبانی تا پایه های روشنایی، تابلو WELL XX-DP03 تغذیه شونده از سوئیچگیر به صورت مجزا در نظر گرفته شده است.
3 | Lighting layouts for buidlings and outdoor area shall be added as reference document. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | اعمال گردید.
4 | According to our telephone conversation following items shall be added or modified: |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23
4-1 | Considered seperat sub-bus for outdoor wallmounted lighting feeder in single line diagram shall be deleted. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | حذف گردید.
4-2 | Installation type of lighting panels (Surface/Flush mounted) shall be specified in table. (Note 1 shall be modified base on installation type.) |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | اعمال گردید.
5 | Security building SLD: Type of CB. for feeder 7 shall be modified. (shall be considered RCBO instead of MCB) |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | اعمال گردید.
6 | Security building SLD: MCB technical description for feeders NO. 7&9 shall be added on SLD. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | اعمال گردید.
7 | Outgoing cables form switchgear building lighting panel to diesel generator shelter shall be armour type. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | با توجه به این موضوع که مکان دیزل ژنراتور نهایی نشده است در صورتیکه کابل روشنایی آن زیرزمینی باشد، از کابل آرموردار استفاده خواهد شد. لازم به ذکر است در ویرایش های بعدی معماری آن تکمیل و در این مدرک روشنایی آن نمایش داده خواهد شد.
8 | Complementary comments will be submitted after received revised document. |  | BK-SUR-ENG-ELE-01-04393 | 2022-05-23 | در صورت وجود کامنت احتمالی متعاقبا بررسی خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 23-May-22 |  |  |  |  | Date: