## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-EL-LI-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1026 |  |  | Transmital Date: 31-May-2022
Document Title: Electrical power & control cable list in siahmakan gas injection |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1026 |  |  | Transmital Date: 31-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-PPL-PEDCO-320-EL-LI-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | محاسبات سایز کابل در یک صفحه از مدرک ارائه گردد. |  | 1401-2294-111571 | 1401-03-31 | در ادامه جدول کابل و در زیر آن نحوه محاسبات کابل مشخص شده است. افت ولتاژ با توجه به سایزهای مختلف و طول کابل، محاسبه و برای همه انواع کابل یک درصد درنظر گرفته شده است. از آنجا که فاصله دقیق پست موجود تا محل ترانس رکتیفایر نهایی نشده است، بیشترین فاصله و بزرگترین سایز کابل در این زمان انتخاب و در نظر گرفته می شود تا در ویرایش های بعدی تکمیل گردد.
2 | به نظر می رسد طول مسیر کابل از کلیدخانه موجود تا ترانس حفاظت کاتدی خیلی بیشتر از مقدار موجود در جدول باشد. لازم است موضوع بررسی و طول کابل اصلاح گردد. |  | 1401-2294-111571 | 1401-03-31 | مطابق با توضیحات ارائه شده طول کابل حدود 270 متر و با سایز 70*4 در نظر گرفته شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 14-Jun-2022 |  |  |  |  | Date: