## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-PPL-PEDCO-320-EL-LI-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1026 |  |  | Transmital Date: 31-May-2022
Document Title: Electrical power & control cable list in siahmakan gas injection |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1026 |  |  | Transmital Date: 31-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-PPL-PEDCO-320-EL-LI-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | It shall be revised after finalizing or minor comments on electrical load list in siahmakan gas injection. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | بیشترین توان بار برای این ترانس یعنی 15 کیلووات در نظر گرفته شده است. در صورت انجام محاسبه نهایی، این عدد مورد ویرایش قرار خواهد گرفت.
2 | Cable type shall be completely mentioned in cable list such as conductor type, inner and outer insulation (XPLE or PVC), armour, Screen, etc in legend sheet. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | نوع کابل به صورت CU/XLPE/SWA/PVC در نظر گرفته شده است.
3 | Gland type(Ex or Non-ex) and size shall be specified. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | مشخص گردید.
4 | According to scope of work, cable length shall be rechecked and modified (if required). |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | طول کابل مشخص گردید.
5 | Reference document for OD cables and gland size shall be attached to document and submitted in next revision to check OD cables and gland size. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | مرجع کابل ابهر می باشد. که پیوست می گردد.
6 | Tag number of cable shall be modified according to cable tag numbering procedure in legend sheet. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | تگ نامبر کابل حذف گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 14-Jun-2022 |  |  |  |  | Date: