## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: |  |  |  | MECHANICAL DATA SHEETS FOR FIRE WATER PUMPS-DIESEL ENGINE DRIVEN | [9 empty] | شماره صفحه: 1 از 13
053-073-9184 |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه
|  |  |  | BK | GCS | PEDCO | 120 | ME | DT |  | 0030 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
MECHANICAL DATA SHEETS FOR FIRE WATER MAIN PUMPS-DIESEL ENGINE DRIVEN (P-2301 B) نگهداشت و افزایش تولید میدان نفتی بینک
D03 | OCT. 2022 | IFA |  |  |  |  | H. Adineh |  |  | M. Fakharian |  |  | M. Mehrshad
D02 | JUL. 2022 | IFA |  |  |  |  | H. Adineh |  |  | M. Fakharian |  |  | M. Mehrshad
D01 | APR. 2022 | IFA |  |  |  |  | H. Adineh |  |  | M. Fakharian |  |  | M. Mehrshad
D00 | FEB. 2022 | IFC |  |  |  |  | H. Adineh |  |  | M. Fakharian |  |  | M. Mehrshad
Rev. | Date | Purpose of Issue / Status |  |  |  |  | Prepared by: |  |  | Checked by: |  |  | Approved by: |  | CLIENT Approval
Class: 2 CLIENT Doc. Number: F0Z-708861
status: |  |  | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## Record Sheet
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: |  |  |  |  | MECHANICAL DATA SHEETS FOR FIRE WATER PUMPS-DIESEL ENGINE DRIVEN | [9 empty] | شماره صفحه: 2 از 13
053-073-9184 |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه
[5 empty] | BK | GCS | PEDCO |  | 120 | ME |  | DT | 0030 | D03
REVISION RECORD SHEET
| page | D00 | D01 | D02 |  | D03 |  | D04 |  |  | page |  | D00 | D01 | D02 | D03 | D04
| 1 | X | X | X |  | X |  |  |  |  | 65
| 2 | X | X | X |  | X |  |  |  |  | 66
| 3 | X | X | X |  | X |  |  |  |  | 67
| 4 | X | [8 empty] | 68
| 5 | X | X | X |  | X |  |  |  |  | 69
| 6 | X | X | X |  | X |  |  |  |  | 70
| 7 | X | [8 empty] | 71
| 8 | X | [8 empty] | 72
| 9 | X | [8 empty] | 73
| 10 | X | X | X | [6 empty] | 74
| 11 | X |  | X | [6 empty] | 75
| 12 | X |  | X | [6 empty] | 76
| 13 | X | X | [7 empty] | 77
| 14 | [9 empty] | 78
| 15 | [9 empty] | 79
| 16 | [9 empty] | 80
| 17 | [9 empty] | 81
| 18 | [9 empty] | 82
| 19 | [9 empty] | 83
| 20 | [9 empty] | 84
| 21 | [9 empty] | 85
| 22 | [9 empty] | 86
| 23 | [9 empty] | 87
| 24 | [9 empty] | 88
| 25 | [9 empty] | 89
| 26 | [9 empty] | 90
| 27 | [9 empty] | 91
| 28 | [9 empty] | 92
| 29 | [9 empty] | 93
| 30 | [9 empty] | 94
| 31 | [9 empty] | 95
| 32 | [9 empty] | 96
| 33 | [9 empty] | 97
| 34 | [9 empty] | 98
| 35 | [9 empty] | 99
| 36 | [9 empty] | 100
| 37 | [9 empty] | 101
| 38 | [9 empty] | 102
| 39 | [9 empty] | 103
| 40 | [9 empty] | 104
| 41 | [9 empty] | 105
| 42 | [9 empty] | 106
| 43 | [9 empty] | 107
| 44 | [9 empty] | 108
| 45 | [9 empty] | 109
| 46 | [9 empty] | 110
| 47 | [9 empty] | 111
| 48 | [9 empty] | 112
| 49 | [9 empty] | 113
| 50 | [9 empty] | 114
| 51 | [9 empty] | 115
| 52 | [9 empty] | 116
| 53 | [9 empty] | 117
| 54 | [9 empty] | 118
| 55 | [9 empty] | 119
| 56 | [9 empty] | 120
| 57 | [9 empty] | 121
| 58 | [9 empty] | 122
| 59 | [9 empty] | 123
| 60 | [9 empty] | 124
| 61 | [9 empty] | 125
| 62 | [9 empty] | 126
| 63 | [9 empty] | 127
| 64 | [9 empty] | 128

## Notes
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: |  |  | MECHANICAL DATA SHEETS FOR FIRE WATER PUMPS-DIESEL ENGINE DRIVEN | [7 empty] | شماره صفحه: 3 از 13
053-073-9184 |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | PEDCO | 120 | ME | DT | 0030 | D03
GENERAL NOTES
| 1 | Vendor shall fill in the blanks and return the completed data sheet along with Diesel data sheet with his proposal.
| 2 | Vendor shall submit ITP (Inspection & Testing Plan) with his proposal.
| 3 | Vendor is requested to confirm the material, or propose appropriate alternative.
| 4 | For Instrumentation, Project specification 'Specification For Instrument and Control of package Unit System (PU)' Doc. No.
BK-GNRAL-PEDCO-000-IN-SP-0004. shall be followed.
| 5 | Instead of mechanical seal, vendor shall advise the suitable Packing specification.
| 6 | NPSH test shall be done & witnessed if the margin of NPSHr & NPSHa is less than 1.
| 7 | The Tie-in flanges shall conform to ASME B-16.1.
| 8 | Pump drain shall be terminated at skid edge with flange connection and valved.
| 9 | Supplier to indicate which minimum flow pumps can achieve.
| 10 | Nozzle loads shall be 2 times the loads shown in API 610 11th Edition.
| 11 | The Suction line size is 12" and discharge line is 10" .
| 12 | Air release valve shall be considered by vendor .
| 13 | As the pump jobsite environmental condition is fumy and dusty, any required protection for pumps, panels and electrical parts
(in accordance with IPS-E-EL-100) in this regard shall be considered by pump manufacturer.
| 14 | Ultrasonic Test shall be performed for forged shaft.
| 15 | Couplings shall be dry, flexible and spacer type.
| 16 | A local control panel shall be considered by vendor to be located next to the pumps as per "Specification For Fire Water
Pumps", Doc. No. BK-GCS-PEDCO-120-ME-SP-0005'. Alarm and trip shall be specified for diesel control based on NFPA 20.
| 17 | Pump LCP shall be designed to manage all required monitoring and control signals , as minimum in accordance with
"P&ID For Fire Water Network", Doc.No.BK-GCS-PEDCO-120-SA-PI-0001.
| 18 | The electrical characteristics of panels shall be specified by vendor such as: - The power demand of control panel. - The number of control panel.
| 19 | Fuel daily tank shall be sized for 8 hours and all instruments such as level transmitter with HH/LL Alarm and etc. are in vendor's scope of supply.
| 20 | Diesel engine shall be tested at 110% rated speed in mechanical running test also the maximum speed of diesel engines shall be 2300 RPM.
| 21 | pressure sensing lines are in the vendor's scope of supply.
| 22 | The sparate power & control panels for main pump diesel engine shall be considered by vendor. Therefore required single line, wiring diagram and etc.
shall be specified by vendor.
| 23 | Design pressure is 15.4 barg also as per NFPA 20 standard the hydrotest pressure shall not be less than 17.24 barg.
| 24 | Estimated BHP at rated capacity is 199.2 kW by considering 65% efficiency.
| 25 | The pumps shall furnish not less than 150% of rated capacity at not less than 65% of rated head.
D03

## P-2301 B (1)
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: | [5 empty] | MECHANICAL DATA SHEETS FOR FIRE WATER PUMPS-DIESEL ENGINE DRIVEN | [12 empty] | شماره صفحه: 4 از 13
053-073-9184 | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه
[6 empty] | BK |  | GCS |  | PEDCO |  | 120 | ME | DT | 0030 |  | D03
CENTRIFUGAL PUMP DATA SHEET (SI UNIT) - P-2301 B (Sheet 1 of 6)
[9 empty] | CLIENT: |  | National Iranian South Oil Company (NISOC)
[9 empty] | PROJECT TITLE: |  | BINAK Gas Compressor Station
JOB NUMBER:
[9 empty] | EQUIPMENT NUMBER: |  | P-2301 B
[9 empty] | EQUIPMENT SERVICE: |  | Fire Water Pumps - Diesel Engine Driven
SERIAL NUMBER:
[9 empty] | REQ. / SPEC NO. : |  | BK-GCS-PEDCO-120-ME-SP-0005
PURCH ORDER NO.
|  | Cells coloured thus |  |  |  |  | contain drop-down options
contain calculated values based on input data; do not change.
identify a cross referenced paragraph in the document note, and may also contain a drop down list
When you have completed the DS, highlight the whole page format cells pattern none
Delete these notes on completion
COMMENTS:
DATA SHEETS
|  |  |  | ITEM No. |  |  |  |  | ATT |  | ITEM No. |  |  |  |  | ATT |  | ITEM No. |  | ATT
| PUMP |  |  | P-2301 B |  |  |  |  | YES
MOTOR
GEAR
TURBINE

## P-2301 B (2)
NISOC | [10 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: | [10 empty] | MECHANICAL DATA SHEETS FOR FIRE WATER PUMPS-DIESEL ENGINE DRIVEN | [16 empty] | شماره صفحه: 5 از 13
053-073-9184 | [10 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه
[11 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | ME |  | DT |  | 0030 |  | D03
CENTRIFUGAL PUMP DATA SHEET (SI UNIT) - P-2301 B (Sheet 2 of 6)
APPLICABLE TO: |  |  |  |  | PROPOSAL | [13 empty] | APPLICABLE NTL/INTNTL STANDARD: | [6 empty] | NFPA20 (2019) & IPS-M-PM-125
FOR |  |  | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC |  | UNIT
SITE |  |  | BINAK Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station |  | SERVICE |  |  | Fire Water Pumps - Diesel Engine Driven
NO. REQ |  |  | 1 | [5 empty] | PUMP SIZE | [9 empty] | TYPE | [6 empty] | No. STAGES
MANUFACTURER | [18 empty] | MODEL |  |  | BB1 (V.T.C) |  |  |  | SERIAL NO.
LIQUID CHARACTERISTICS
[8 empty] | Units |  |  | Maximum |  |  | Minimum |  |  | Note |  |  | SERVICE : | [9 empty] | INTERMITTENT
LIQUID TYPE OR NAME : | [7 empty] | Water | [8 empty] | Max & min |  |  | • IF INTERMITTENT NO. OF STARTS :
VAPOR PRESSURE : | [7 empty] | bara |  |  | 0.0087 |  |  | 0.1219 |  |  | values refer |  |  | PUMPS OPERATE IN:
DENSITY : | [7 empty] | kg/m³ |  |  | 997 | [5 empty] | only to the |  |  | CORROSION DUE TO : (6.12.1.9)
SPECIFIC HEAT : | [7 empty] | kj/kgC |  |  | 4.186 |  |  | 4.186 |  |  | property |  |  | EROSION DUE TO : (6.12.1.9)
VISCOSITY : | [7 empty] | cP |  |  | 1 | [5 empty] | listed |  |  | H2S CONCENTRATION (ppm) : (6.12.1.12) | [11 empty] | N.A.
OPERATING CONDITIONS (6.1.2) | [19 empty] | CHLORIDE CONCENTRATION (ppm) :
[8 empty] | Units |  |  | Maximum |  |  | Rated |  | Normal |  | Min |  | PARTICULATE SIZE (DIA IN MICRONS)
NPSHA Datum: | [10 empty] | C.L. Impeller | [8 empty] | PARTICULATE CONCENTRATION (PPM)
PUMPING TEMPERATURE : | [7 empty] | oC |  |  | 50 | [6 empty] | 5
FLOW : | [7 empty] | m3/hr | [5 empty] | 454.2
DISCHARGE PRESSURE :(6.3.2) | [7 empty] | barg | [5 empty] | 10.4
SUCTION PRESSURE : | [7 empty] | barg |  |  | 0.83 |  |  | 0.814 |  |  |  | 0.08
DIFFERENTIAL PRESSURE : | [7 empty] | bar | [5 empty] | 10.32
DIFFERENTIAL HEAD : | [7 empty] | m | [5 empty] | 105
NPSHA : | [7 empty] | m | [5 empty] | 8.8
HYDRAULIC POWER: | [7 empty] | KW | [5 empty] | 129.5
SITE AND UTILITY DATA
LOCATION: | [19 empty] | COOLING WATER :
|  | OUTDOOR |  |  |  |  | UNHEATED |  |  |  |  | UNDER ROOF | [13 empty] | RETURN |  |  | DESIGN
MOUNTED AT : | [10 empty] | l | TROPICALISATION REQ'D | [8 empty] | TEMP |  |  |  | MAX
ELECTRIC AREA CLASSIFICATION: | [9 empty] | (6.1.22) |  |  | ZONE |  | SAFE | [5 empty] | PRESS. |  |  |  | MIN
GROUP | [10 empty] | TEMP CLASS | [9 empty] | SOURCE
SITE DATA : | [20 empty] | COOLING WATER CHLORIDE CONCENTRATION: | [10 empty] | ppm
ELEVATION (MSL) : | [5 empty] | 12.5 |  | m |  |  |  | BAROMETER : |  |  |  | 990.77 |  | mBar |  | INSTRUMENT AIR : | [6 empty] | kg |  | MIN |  |  | kg
RANGE OF DESIGN TEMPS:MIN / MAX | [10 empty] | 5 |  |  | 85 |  | oC |  |  |  | STEAM
RELATIVE HUMIDITY: MIN / MAX | [10 empty] | 0 |  |  | 100 |  | % | (@ 25.6 oC) | [6 empty] | DRIVERS |  |  | HEATING
UNUSUAL CONDITIONS: | [12 empty] | NA | [7 empty] | TEMP
UTILITY CONDITIONS : | [20 empty] | PRESS. |  | kg
ELECTRICITY : |  |  |  |  | AUXILIARY |  |  | HEATING |  |  | CONTROL |  |  | SHUTDOWN
| VOLTAGE |  |  |  | 400
| PHASE |  |  |  | 3
| HERTZ |  |  |  | 50
PERFORMANCE | [19 empty] | DRIVER (7.1.5) (NOTE 22)
PROPOSAL CURVE NO. | [11 empty] | RPM | [7 empty] | Driver Type | [9 empty] | DIESEL ENGINE
| As Tested Curve No. | [18 empty] | GEAR | [10 empty] | NO
IMPELLER DIA.: |  |  |  | RATED |  |  |  | MAX. |  |  |  | MIN. |  |  |  | mm |  |  |  | VARIABLE SPEED REQUIRED | [10 empty] | NO
RATED POWER | [6 empty] | Kw |  |  | EFFICIENCY | [5 empty] | (%) |  |  |  | SOURCE OF VARIABLE SPEED
RATED CURVE BEP FLOW (at rated impeller dia) | [15 empty] | m³/hr |  |  |  | OTHER
MIN FLOW : |  |  |  | THERMAL |  |  |  | kJ/Nm³ |  |  |  | STABLE |  |  |  | m³/hr |  |  |  | MANUFACTURER
PREFERRED OPERATING REGION (6.1.11) | [12 empty] | to |  |  | m³/hr |  |  |  | NAMEPLATE POWER |  |  |  |  | @Site Condition | [7 empty] | KW
ALLOWABLE OPERATING REGION | [12 empty] | to |  |  | m³/hr |  |  |  | Nominal RPM
MAX HEAD @ RATED IMPELLER | [15 empty] | m |  |  |  | RATED LOAD RPM
MAX POWER @ RATED IMPELLER | [15 empty] | kW |  |  |  | FRAME OR MODEL
NPSH3 AT RATED FLOW : | [15 empty] | m |  |  |  | ORIENTATION | [7 empty] | HORIZONTAL
CL PUMP TO U/S BASEPLATE | [15 empty] | m |  |  |  | LUBE
NPSH MARGIN AT RATED FLOW : | [15 empty] | m
SPECIFIC SPEED (6.1.9) | [19 empty] | RADIAL | [9 empty] | /
SUCTION SPECIFIC SPEED LIMIT | [19 empty] | THRUST | [9 empty] | /
SUCTION SPECIFIC SPEED | [19 empty] | STARTING METHOD
MAX. ALLOW. SOUND PRESS. LEVEL REQD (6.1.14) | [13 empty] | 110 |  | (dBA) |  | @ 1 m |  | SEE DRIVER DATA SHEET
EST MAX SOUND PRESS. LEVEL | [15 empty] | (dBA) |  |  |  | Max Voltage Variation
MAX. SOUND POWER LEVEL REQ'D (6.1.14) | [19 empty] | Max Frequency Variation
EST MAX SOUND POWER LEVEL | [19 empty] | Max Voltage and Frequency Variation together
D03

## P-2301 B (3)
NISOC | [7 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: | [7 empty] | MECHANICAL DATA SHEETS FOR FIRE WATER PUMPS-DIESEL ENGINE DRIVEN | [15 empty] | شماره صفحه: 6 از 13
053-073-9184 | [7 empty] | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه
[8 empty] | BK |  | GCS |  | PEDCO | 120 |  | ME |  | DT |  | 0030 |  |  | D03
CENTRIFUGAL PUMP DATA SHEET (SI UNIT) - P-2301 B (Sheet 3 of 6)
CONSTRUCTION
API PUMP TYPE: |  |  | BB1 |  | [Based on API 610 definitions] | [10 empty] | CASING MOUNTING:
[16 empty] | CASING TYPE: | [5 empty] | (6.3.10)
NOZZLE CONNECTIONS: |  |  |  |  | (6.5.5) |  |  | NOTES 7,11 | [7 empty] | OH3 BACKPULLOUT LIFTING DEVICE REQD. (9.1.2.6)
|  |  |  | Size |  | Facing |  | Rating |  |  | Position | [5 empty] | CASE PRESSURE RATING:
SUCTION | [5 empty] | FF |  | 125 |  |  | SIDE | [7 empty] | MAWP : | MAWP : |  | (6.3.5) |  | By vendor |  | barg | @ |  |  |  | oC
DISCHARGE | [5 empty] | FF |  | 125 |  |  | SIDE | [7 empty] | HYDROTEST : |  |  |  |  | 1.5*MAWP |  | barg | @ |  |  |  | oC
PRESSURE CASING AUX. CONNECTIONS: (6.4.3.2)
|  | No. |  | Size |  | Type |  | Facing |  | Rating |  | Posn. |  |  |  |  | HYDROTEST OH PUMP AS ASSEMBLY | [10 empty] | YES
BAL./LEAK OFF | [16 empty] | SUCT'N PRESS. REGIONS DESIGNED FOR MAWP | [10 empty] | YES
DRAIN | [16 empty] | ROTATION: |  |  |  | (VIEWED FROM COUPLING END)
VENT | [17 empty] | • | IMPELLERS INDIVIDUALLY SECURED :
PRESSURE GAGE | [17 empty] | • | BOLT OH 3/4/5 PUMP TO PAD / FOUNDATION :
TEMP GAGE | [17 empty] | • | PROVIDE SOLEPLATE FOR OH 3/4/5 PUMPS
WARM-UP LINE | [16 empty] | ROTOR:
SHAFT FLEXIBILITY INDEX (SFI) (9.1.1.3)
| Drain Valve Supplied By | [8 empty] | SUPPLIER | [6 empty] | First Critical Speed Wet (Multi stage pumps only)
| DRAINS MANIFOLDED | [8 empty] | YES | [6 empty] | COMPONENT BALANCE TO ISO 1940 G1.0 | [10 empty] | NO
| VENT Valve Supplied By | [8 empty] | SUPPLIER | [6 empty] | SHRINK FIT -LIMITED MOVEMENT IMPELLERS (9.2.2.3)
| VENTS MANIFOLDED | [8 empty] | YES | [6 empty] | COUPLING:(7.2.3) | [5 empty] | (7.2.13.f) |  | NOTE 16
| THREAD. CONS FOR PIPELINE SERVICE & < 50°C (6.4.3.2) | [10 empty] | NO |  |  |  |  | MANUFACTURER
| SPECIAL FITTINGS FOR TRANSITIONING (6.4.3.3) | [10 empty] | NO |  |  |  |  | MODEL
| CYLINDRICAL THREADS REQUIRED (6.4.3.8) | [10 empty] | NO |  |  |  |  | RATING (POWER/100 RPM)
| GUSSET SUPPORT REQUIRED | [10 empty] | YES |  | If Needed |  |  | SPACER LENGTH | [12 empty] | mm
| MACHINED AND STUDDED CONNECTIONS (6.4.3.12) | [10 empty] | NO |  |  |  |  | SERVICE FACTOR | [10 empty] | Min 1.5
| VS 6 DRAIN | [8 empty] | N/A | [6 empty] | RIGID | [10 empty] | NO
| DRAIN TO SKID EDGE | [10 empty] | YES |  |  |  |  | COUPLING WITH HYDRAULIC FIT (7.2.10)
MATERIAL (6.12.1.1) | [16 empty] | COUPLING BALANCED TO ISO 1940-1 G6.3 (7.2.3) | [10 empty] | YES
APPENDIX H CLASS | [6 empty] | I-2 |  |  | NOTES 3 | [6 empty] | COUPLING WITH PROPRIETARY CLAMPING DEVICE (7.2.11)
MIN DESIGN METAL TEMP (6.12.4.1) | [10 empty] | 5 |  |  | °C
REDUCED-HARDNESS MATERIALS REQ'D (6.12.1.12.1) | [16 empty] | COUPLING IN COMPLIANCE WITH (7.2.4) | [8 empty] | API 671
Applicable Hardness Standard (6.12.1.12.3) | [16 empty] | COUPLING GUARD STANDARD PER (7.2.13.a) | [9 empty] | ISO 14120
BARREL : | [16 empty] | Window on Coupling Guard
CASE :
DIFFUSERS | [15 empty] | BASEPLATE
IMPELLER : | [16 empty] | API BASEPLATE NUMBER :
IMPELLER WEAR RING : | [16 empty] | BASEPLATE CONSTRUCTION (7.3.14)
CASE WEAR RING : | [16 empty] | BASEPLATE DRAINAGE (7.3.1) | [7 empty] | Entire Baseplate Drain Pan
SHAFT: | [16 empty] | MOUNTING :
Bowl (if VS-type) | [16 empty] | NON-GROUT CONSTRUCTION : (7.3.13)
Inspection Class Note 2 | [16 empty] | VERTICAL LEVELING SCREWS : | [7 empty] | REQUIRED
BEARINGS AND LUBRICATION (6.10.1.1) | [16 empty] | LONGITUDINAL DRIVER POSITIONING SCREWS : | [9 empty] | REQUIRED
BEARING (TYPE / NUMBER): |  |  |  |  | (6.11.4) | [11 empty] | SUPPLIED WITH : |  |  |  |  | l | GROUT AND VENT HOLES | [5 empty] | YES
| RADIAL |  |  |  |  | / | [15 empty] | l | DRAIN CONNECTION | [5 empty] | YES
| THRUST |  |  |  |  | / | [10 empty] | MOUNTING PADS SIZED FOR BASEPLATE LEVELING (7.3.5) | [11 empty] | YES
REVIEW AND APPROVE THRUST BEARING SIZE : (9.2.5.2.4) | [16 empty] | MOUNTING PADS TO BE MACHINED (7.3.6) | [11 empty] | YES
[17 empty] | PROVIDE SPACER PLATE UNDER ALL EQUIPMENT FEET | [11 empty] | YES
LUBRICATION : |  | (6.10.2.2) (6.11.3) (9.2.6) | [14 empty] | OTHER
| PRESSURE LUBE SYSTEM TO ISO 10438- | [8 empty] | (9.2.6.5)
ISO 10438 DATA SHEETS ATTACHED
| Pressurized Lube Oil System mtd on pump baseplate | [15 empty] | REMARKS :
Location of Pressurized Lube Oil System mounted on baseplate :
| INTERCONNECTING PIPING PROVIDED BY | [8 empty] | Supplier
| OIL VISC. ISO GRADE | [7 empty] | VG
CONSTANT LEVEL OILER :
D03

## P-2301 B (4)
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: |  |  |  | MECHANICAL DATA SHEETS FOR FIRE WATER PUMPS-DIESEL ENGINE DRIVEN | [11 empty] | شماره صفحه: 7 از 13
053-073-9184 |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک |  | سریال |  | نسخه
|  |  |  | BK | GCS | PEDCO | 120 | ME |  | DT |  | 0030 |  | D03
CENTRIFUGAL PUMP DATA SHEET (SI UNIT) - P-2301 B (Sheet 4 of 6)
INSTRUMENTATION | [8 empty] | SEAL SUPPORT SYSTEM MOUNTING
SEE ATTACHED API-670 DATA SHEET | [9 empty] | SEAL SUPPORT SYSTEM MOUNTED ON PUMP BASEPLATE
ACCELEROMETER (7.4.2.1) | [16 empty] | (7.5.1.4)
| Number of Accelerometers | [8 empty] | IDENTIFY LOCATION ON BASEPLATE
Mounting Location of Accelerometers
[10 empty] | INTERCONNECTING PIPING BY | [7 empty] | Supplier
| PROVISION FOR MTG ONLY |  | (6.10.2.10) |  |  | YES
| Number of Accelerometers | [7 empty] | MECHANICAL SEAL (6.8.1)
| Mounting Location of Accelerometers | [8 empty] | SEE ATTACHED ISO 21049/API 682 DATA SHEET | [9 empty] | N / A | NOTE 5
[10 empty] | ADDITIONAL CENTRAL FLUSH PORT | [6 empty] | (6.8.9)
| FLAT SURFACE REQUIRED |  | (6.10.2.11) |  |  | N / A |  |  |  | HEATING JACKET REQ'D. | [6 empty] | (6.8.11) |  |  | N / A
| Number of Accelerometers | [8 empty] | FLUSH PLAN
Mounting Location of Accelerometers
VIBRATION PROBES (7.4.2.2) | [5 empty] | N / A |  |  | HEATING AND COOLING (6.1.17)
| PROVISIONS FOR VIB. PROBES | [8 empty] | COOLING REQ'D | [9 empty] | NO
| NUMBER PER RADIAL BEARING | [8 empty] | COOLING WATER PIPING PLAN
| NUMBER PER AXIAL BEARING | [8 empty] | COOLING WATER PIPING
FITTINGS
| MONITORS AND CABLES SUPPLIED BY (7.4.2.4) | [8 empty] | COOLING WATER PIPING MATERIALS
COOLING WATER REQUIREMENTS:
TEMPERATURE (7.4.2.3) | [18 empty] | BEARING HOUSING
| PROVISIONS FOR TEMP PROBES | [17 empty] | HEAT EXCHANGER
| RADIAL BEARING TEMP. | [8 empty] | TOTAL COOLING WATER
|  | NUMBER PER RADIAL BEARING | [7 empty] | HEATING MEDIUM
| THRUST BEARING TEMP. | [9 empty] | OTHER
|  | NUMBER PER THRUST BEARING ACTIVE SIDE | [7 empty] | HEATING PIPING
NUMBER PER THRUST BEARING INACTIVE SIDE
| TEMP. GAUGES (WITH THERMOWELLS) (9.1.3.6) | [7 empty] | PIPING & APPURTENANCES
| PRESSURE GAUGE TYPE | [8 empty] | MANIFOLD PIPING FOR PURCHASER CONNECTION (7.5.1.6)
| Remarks | [11 empty] | VENT |  |  |  |  | YES
[13 empty] | DRAIN |  |  |  |  | YES
[13 empty] | VALVES |  |  |  |  | YES (NOTE 8)
[13 empty] | COOLING WATER | [6 empty] | NO
[11 empty] | TAG ALL ORIFICES (7.5.2.4) | [8 empty] | YES
SOCKET WELD CONN ON SEAL GLAND (7.5.2.8)

## P-2301 B (5)
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: | [5 empty] | MECHANICAL DATA SHEETS FOR FIRE WATER PUMPS-DIESEL ENGINE DRIVEN | [14 empty] | شماره صفحه: 8 از 13
053-073-9184 | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات | رشته |  | نوع مدرک |  | سریال |  | نسخه
[6 empty] | BK |  | GCS |  | PEDCO | 120 | ME |  | DT |  | 0030 |  | D03
CENTRIFUGAL PUMP DATA SHEET (SI UNIT) -P-2301 B (Sheet 5 of 6)
SURFACE PREPARATION AND PAINT | [12 empty] | TEST
MANUFACTURER'S STANDARD | [13 empty] | SHOP INSPECTION (8.1.1) | [11 empty] | Yes
OTHER (SEE BELOW) | [13 empty] | PERFORMANCE CURVE
SPECIFICATION NO. |  |  | BK-GNRAL-PEDCO-000-PI-SP-0006, "Specification | [10 empty] | & DATA APPROVAL PRIOR TO SHIPMENT. | [11 empty] | YES
|  |  | for Painting" | [10 empty] | TEST WITH SUBSTITUTE SEAL (8.3.3.2.b)
PUMP: | [13 empty] | MATERIAL CERTIFICATION REQUIRED | [9 empty] | CASING |  | YES
PUMP SURFACE PREPARATION | [13 empty] | SHAFT |  |  | YES |  |  |  | (6.12.1.8) |  |  | IMPELLER |  | YES
PRIMER |  |  |  |  | AS PER PROJECT PAINTING SPEC. | [8 empty] | OTHER |  |  | YES |  | Casing and impeller Wear ring
FINISH COAT |  |  |  |  | AS PER PROJECT PAINTING SPEC. | [8 empty] | CASTING REPAIR WELD PROCEDURE APPR REQD | [11 empty] | YES
BASEPLATE: | [13 empty] | INSPECTION REQUIRED FOR CONNECTION WELDS (6.12.3.4.d)
BASEPLATE SURFACE PREPARATION | [13 empty] | LIQUID PENETRANT |  |  |  |  | YES |  |  | MAG PARTICLE
PRIMER: |  |  |  |  | AS PER PROJECT PAINTING SPEC. | [8 empty] | ULTRASONIC | [7 empty] | RADIOGRAPHY |  |  |  | YES
FINISH COAT |  |  |  |  | AS PER PROJECT PAINTING SPEC. | [8 empty] | INSPECTION REQUIRED FOR CASTINGS
DETAILS OF LIFTING DEVICES | [13 empty] | LIQUID PENETRANT |  |  |  |  | YES |  |  | MAG PARTICLE |  |  |  | YES
SHIPMENT: (8.4.1) | [7 empty] | EXPORT | [5 empty] | ULTRASONIC |  |  |  |  | YES |  |  | RADIOGRAPHY
EXPORT BOXING REQUIRED | [9 empty] | YES |  |  |  | HARDNESS TEST REQUIRED (8.2.2.7)
OUTDOOR STORAGE MORE THAN 6 MONTHS | [9 empty] | YES |  |  |  | ADDNL SUBSURFACE EXAMINATION (6.12.1.5) (8.2.1.3)
SPARE ROTOR ASSEMBLY PACKAGED FOR: | [21 empty] | FOR
ROTOR STORAGE ORIENTATION (9.2.8.2) | [21 empty] | METHOD
SHIPPING & STORAGE CONTAINER FOR VERT STORAGE (9.2.8.3)
N2 PURGE (9.2.8.4) | [13 empty] | PMI TESTING REQUIRED (8.2.2.8)
SPARE PARTS | [14 empty] | COMPONENTS TO BE TESTED
START-UP | [9 empty] | YES |  |  |  | RESIDUAL UNBALANCE TEST (J.4.1.2)
NORMAL MAINTENANCE | [9 empty] | YES |  |  |  | NOTIFICATION OF SUCCESSFUL SHOP | [11 empty] | YES
|  |  |  | WEIGHTS |  | Kg | [7 empty] | PERFORMANCE TEST (8.1.1.c) (8.3.3.5) | [11 empty] | YES
ITEM No |  | PUMP | DRIVER |  | GEAR |  | BASE |  |  | TOTAL |  |  |  | BASEPLATE TEST (7.3.21)
[14 empty] | HYDROSTATIC | [10 empty] | WIT
HYDROSTATIC TEST OF BOWLS & COLUMN (9.3.13.2)
[14 empty] | PERFORMANCE TEST | [10 empty] | WIT
OTHER PURCHASER REQUIREMENTS | [13 empty] | TEST IN COMPLIANCE WITH (8.3.3.2) | [10 empty] | NFPA 20
| COORDINATION MEETING REQUIRED (10.1.3) | [8 empty] | YES |  |  |  | TEST DATA POINTS TO (8.3.3.3) | [10 empty] | NFPA 20
| MAXIMUM DISCHARGE PRESSURE TO INCLUDE | [12 empty] | TEST TOLERANCES TO (8.3.3.4) | [10 empty] | TABLE 16
[9 empty] | MAX RELATIVE DENSITY |  |  |  |  | NPSH (8.3.4.3.1) (8.3.4.3.4) | [8 empty] | NOTE 6 |  | WIT
| OPERATION TO TRIP SPEED | [12 empty] | NPSH-1ST STG ONLY (8.3.4.3.2)
| MAX DIA. IMPELLERS AND/OR NO OF STAGES | [8 empty] | YES |  |  |  | NPSH TESTING TO HI 1.6 OR ISO 9906 (8.3.4.3.3)
| CONNECTION DESIGN APPROVAL (9.2.1.4) | [8 empty] | YES |  |  |  | TEST NPSHA LIMITED TO 110% SITE NPSHA (8.3.3.6)
| TORSIONAL ANALYSIS / REPORT (6.9.2.10) | [8 empty] | NO |  |  |  | RETEST ON SEAL LEAKAGE (8.3.3.2.d) | [10 empty] | OBSERVE
| PROGRESS REPORTS | [8 empty] | YES |  |  |  | RETEST REQUIRED AFTER FINAL HEAD ADJ (8.3.3.7.b)
| OUTLINE OF PROC FOR OPTIONAL TESTS (10.2.5) | [12 empty] | COMPLETE UNIT TEST (8.3.4.4.1) | [10 empty] | WIT
| ADDITIONAL DATA REQUIRING 20 YEARS RETENTION (8.2.1.1) | [12 empty] | SOUND LEVEL TEST (8.3.4.5) | [10 empty] | WIT
[10 empty] | YES |  |  |  | CLEANLINESS PRIOR TO FINAL ASSEMBLY (8.2.2.6) | [10 empty] | OBSERVE | OBSERVE
| LATERAL ANALYSIS REQUIRED (9.1.3.4) (9.2.4.1.3) | [8 empty] | NO |  |  |  | LOCATION OF CLEANLINESS INSPECTION
| MODAL ANALYSIS REQUIRED (9.3.9.2) | [12 empty] | NOZZLE LOAD TEST
| DYNAMIC BALANCE ROTOR (6.9.4.4) | [8 empty] | YES |  |  |  | CHECK FOR CO-PLANAR MOUNTING PAD SURFACES
| INSTALLATION LIST IN PROPOSAL (10.2.3.l) | [8 empty] | YES |  |  |  | MECHANICAL RUN TEST UNTIL OIL TEMP STABLE
| VFD STEADY STATE DAMPED RESPONSE ANALYSIS (6.9.2.3) | [8 empty] | NO | NO |  |  | 4 HR. MECH RUN AFTER OIL TEMP STABLE (8.3.4.2.1) | [10 empty] | WIT
| TRANSIENT TORSIONAL RESPONSE |  |  |  |  | (6.9.2.4) |  |  |  | NO |  |  |  | 4 HR. MECH RUN TEST (8.3.4.2.2)
| BEARING LIFE CALCULATIONS REQUIRED (6.10.1.6) | [12 empty] | BRG HSG RESONANCE TEST (8.3.4.7)
| IGNITION HAZARD ASSMT TO EN 13463-1 (7.2.13.e) | [12 empty] | STRUCTURAL RESONANCE TEST (9.3.9.2)
| CASING RETIREMENT THICKNESS DRAWING (10.3.2.3) | [12 empty] | REMOVE / INSPECT HYDRODYNAMIC BEARINGS AFTER TEST
| FLANGES RQD IN PLACE OF SKT WELD UNIONS (7.5.2.8) | [13 empty] | (9.2.7.5)
| INCLUDE PLOTTED VIBRATION SPECTRA (6.9.3.3) | [12 empty] | AUXILIARY EQUIPMENT TEST (8.3.4.6)
| CONNECTION BOLTING (7.5.1.7) | [12 empty] | EQUIPMENT TO BE INCLUDED IN AUXILIARY TESTS
| CADMIUM PLATED BOLTS PROHIBITED | [12 empty] | LOCATION OF AUXILIARY EQUIPMENT TEST
| VENDOR TO KEEP REPAIR AND HT RCDS (8.2.1.1.c) | [12 empty] | IMPACT TEST |  |  | (6.12.4.3) |  |  | PER EN 13445
| VENDOR SUBMIT TEST PROCEDURES (8.3.1.1) | [8 empty] | YES | [9 empty] | PER ASME SECTION VIII
| SUBMIT INSPECTION CHECK LIST (8.1.5) NOTE 2 | [8 empty] | YES |  |  |  | REMOVE CASING AFTER TEST

## P-2301 B (6)
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: |  |  |  | MECHANICAL DATA SHEETS FOR FIRE WATER PUMPS-DIESEL ENGINE DRIVEN | [9 empty] | شماره صفحه: 9 از 13
053-073-9184 |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه
|  |  |  | BK | GCS | PEDCO | 120 | ME | DT | 0030 |  | D03
CENTRIFUGAL PUMP DATA SHEET (SI UNIT) - P-2301 B (Sheet 6 of 6)
PRESSURE VESSEL DESIGN CODE REFERENCES
THESE REFERENCES MUST BE LISTED BY THE MANUFACTURER
CASTING FACTORS USED IN DESIGN ( TABLE 3)
SOURCE OF MATERIAL PROPERTIES
WELDING AND REPAIRS (NOTE 12)
THESE REFERENCES MUST BE LISTED BY THE PURCHASER. (DEFAULT TO TABLE 11 IF NO PURCHASER PREFERENCE IS STATED)
ALTERNATE WELDING CODES AND STANDARDS
| WELDING REQUIREMENT (APPLICABLE CODE OR STANDARD) | [11 empty] | DEFAULT PER TABLE 11
| WELDER/OPERATOR QUALIFICATION | [11 empty] | DEFAULT PER TABLE 11
| WELDING PROCEDURE QUALIFICATION | [11 empty] | DEFAULT PER TABLE 11
| NON-PRESSURE RETAINING STRUCTURAL WELDING SUCH AS BASEPLATES OR SUPPORTS | [11 empty] | DEFAULT PER TABLE 11
| MAGNETIC PARTICLE OR LIQUID PENETRANT EXAMINATION OF PLATE EDGES | [11 empty] | DEFAULT PER TABLE 11
| POSTWELD HEAT TREATMENT | [11 empty] | DEFAULT PER TABLE 11
| POSTWELD HEAT TREATMENT OF CASING FABRICATION WELDS | [11 empty] | DEFAULT PER TABLE 11
MATERIAL INSPECTION
| THESE REFERENCES MUST BE LISTED BY THE PURCHASER | [9 empty] | DEFAULT TO TABLE 14 |  |  |  | YES
ALTERNATIVE MATERIAL INSPECTIONS AND ACCEPTANCE CRITERIA (SEE TABLE 15) (8.2.2.5)
| TYPE OF INSPECTION |  |  | METHOD |  |  |  | FOR FABRICATIONS |  |  |  |  | FOR CASTINGS
RADIOGRAPHY
ULTRASONIC INSPECTION
MAGNETIC PARTICLE INSPECTION
LIQUID PENETRANT INSPECTION
VISUAL INSPECTION (all surfaces)
REMARKS :

## Diesel (1)
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: |  | MECHANICAL DATA SHEETS FOR FIRE WATER PUMPS-DIESEL ENGINE DRIVEN | [10 empty] | شماره صفحه: 10 از 13
053-073-9184 |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه
|  | BK |  | GCS | PEDCO | 120 | ME |  | DT | 0030 | D03
Diesel Engine Data Sheet For Fire Water Pump - P-2301 B (SI UNIT) (1 of 4)
SERVICE: | Fire Water Pumps - Diesel Engine Driven | [6 empty] | MANUFACTURER:
FOR: | NISOC | [6 empty] | MODEL NO:
SITE: | BINAK Gas Compressor Station | [6 empty] | TYPE:
NO. REQUIRED: | 1
[5 empty] | (Note 1) | [5 empty] | REMARKS
OPERATING CONDITIONS
DIESEL ENGINE MANUFACTURER
ISO POWER (ISO 3046) |  | kW
ISO SPEED |  | rpm
SITE CONTINUOUS RATED POWER |  | kW
SITE CONTINUOUS RATED SPEED |  | rpm
OVERLOAD SITE POWER |  | kW
OVERLOAD SPEED |  | rpm
OVERLOAD DURATION |  | h
DIRECTION OF ROTATION (FROM CPLG) |  | CW/CCW
SPEED RANGE |  | ±% rpm
IDLE SPEED |  | rpm
LOADING TIME |  | s
PERFORMANCE
% OF MAX CONT SITE POWER
FUEL SPECIFIC CONSUMPTION |  | g/kWh
TOLERANCE |  | %
SPEED |  | rpm | (NOTE 20)
LOAD ACCEPTANCE RATING |  | % 1 step
ENGINE DATA
CYCLE:- 2 STROKE/4 STROKE | [10 empty] | 4 STROKE REQUIRED
NUMBER OF CYLINDERS
IN-LINE/V FORM
BORE/STROKE |  | mm
CAPACITY |  | liters
BMEP (RATED)
PISTON SPEED |  | m/s
COOLING SYSTEM: AIR/WATER | [11 empty] | CLOSED SYSTEM (Air fan & Radiator)
TURBOCHARGER:-
SINGLE OR SERIES
INTERCOOLER |  | CA or CW
EMISSIONS
Nox EMISSION |  | g/kWh | [9 empty] | IPS-E-SF-860
CO EMISSION |  | g/kWh
CO2 EMISSION |  | g/kWh
STARTING SYSTEM
AIR:-
NUMBER OF TANKS
PRESSURE |  | Barg / Kpag
CAPACITY |  | m3
NO. OF STARTS W/OUT REFILLING
STARTING SYSTEM
ELECTRICAL:- | [11 empty] | YES
NO. OF BATTERIES | [10 empty] | 2 Cell (VTC)
TYPE | [11 empty] | Lead-Acid (VTC)
TOTAL CAPACITY |  | Ah
STARTING CIRCUIT
STARTING MOTOR

## Diesel (2)
NISOC | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: | MECHANICAL DATA SHEETS FOR FIRE WATER PUMPS-DIESEL ENGINE DRIVEN | [9 empty] | شماره صفحه: 11 از 13
053-073-9184 | پروژه |  | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
| BK |  | GCS | PEDCO | 120 | ME | DT | 0030 | D03
Diesel Engine Data Sheet For Fire Water Pump - P-2301 B (SI UNIT) (2 of 4)
HYDRAULIC:-
ACCUMULATOR/MOTOR
NO OF STARTS PER 5 SEC CRANKS
NO OF ACCUMULATORS
BARRING SYSTEM
MANUAL/ELEC/HYDRAULIC IF REQ’D | [9 empty] | MANUAL
LUBRICATION
DRY SUMP
SYSTEM;- PRESSURE | bar g / Kpa g
OIL QUANTITY
OIL CONSUMPTION | g/kwh
PUMPS | Main/Aux
OIL FILTER:-
CHANGE OVER WHILE RUNNING | Reqd y/n
INLET SYSTEM
FILTER:- | [9 empty] | TWO STAGE
TYPE | Wet or dry
NUMBER
AIR CUT OFF SYSTEM (“RIG SAVER”) | [9 empty] | YES
EXHAUST SYSTEM
ENGINE PIPE OUTLET | [9 empty] | YES
SPARK ARRESTOR | [9 empty] | YES
SILENCER | dBA @1m | [8 empty] | YES - 85
EXPANSION JOINT | [9 empty] | YES
EXHAUST MANIFOLD | Cooling | [8 empty] | PERSONNEL PROTECTION
FUEL
MAX STATIC HEAD ABOVE FUEL INLET
FILTER CLEANABLE WHILE RUNNING | Y/N | [8 empty] | YES
SELF CLEANING | Y/N | [8 empty] | YES
CHANGEOVER WHILE RUNNING | Y/N | [8 empty] | YES
HEAT EMISSIONS
TO COOLING SYSTEM | kW
TO AMBIENT | kW
SITE AND INSTALLATION DATA
ALTITUDE |  | m
AMBIENT TEMPERATURE MIN/MAX |  | °C | [9 empty] | 5 / 50
DESIGN TEMPERATURE |  | °C | [9 empty] | 52
HUMIDITY |  | % | [9 empty] | 0 / 100
WIND SPEED |  | km/h
ATMOSPHERIC AIR (DUST/FUMES)
CORROSION BY
LOCATION:- INDOOR/OUTDOOR | [9 empty] | OUTDOOR

## Diesel (3)
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: |  |  | MECHANICAL DATA SHEETS FOR FIRE WATER PUMPS-DIESEL ENGINE DRIVEN | [9 empty] | شماره صفحه: 12 از 13
053-073-9184 |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK |  | GCS | PEDCO | 120 | ME | DT | 0030 | D03
Diesel Engine Data Sheet For Fire Water Pump - P-2301 B (SI UNIT) (3 of 4)
HEATED / UNHEATED | [10 empty] | UNHEATED
UNDER ROOF / PARTIAL SIDES | [11 empty] | UNDER ROOF
AREA CLASSIFICATION
STARTING:- LOCAL / REMOTE
AVAILABLE UTILITIES
COOLING WATER:- | [10 empty] | FROM FIRE WATER PUMP DISCHARGE
PRESSURE |  |  |  | bar g / kPa g
AVAILABLE PRESSURE DROP |  |  |  | bar / kPa
TEMPERATURE |  |  |  | °C
TEMPERATURE CHANGE |  |  |  | °C
INSTRUMENT AIR:-
PRESSURE |  |  |  | bar g / kPa g
TEMPERATURE |  |  |  | °C
DEW POINT |  |  |  | °C
ELECTRICITY SUPPLY |  |  |  | AC
DC
FUEL CHARACTERISTICS:-
FUEL OIL CLASSIFICATION
VISCOSITY |  |  |  | cP
TEMPERATURE |  |  |  | °C
OPERATING DURATION |  |  |  | hrs
IMPURITIES |  |  |  | % weight
FUEL SYSTEM
DAY TANK REQUIRED |  | (NOTE 19) | [8 empty] | YES
TANK SUPPLIED BY | [10 empty] | ENGINE SUPPLIER
CAPACITY |  |  |  | hrs | [6 empty] | AS PER NFPA 20
LOCATION | [10 empty] | OFF-SKID
WEIGHTS AND DIMENSIONS
HEAVIEST PART FOR ERECTION
HEAVIEST PART FOR MAINTENANCE
WEIGHT OF ENGINE ONLY
WEIGHT OF SET
WEIGHT OF CONTROL PANEL
HEIGHT UNDER HOOK
DIMENSIONS FOR MAINTENANCE
PAINTING
STANDARD/OTHER | [10 empty] | IPS-E-TP-100
INSPECTION AND TESTING
MANUFACTURER’S STANDARD
OTHER | [10 empty] | IPS-M-PM-290
INSTRUMENTATION | [5 empty] | ALARM |  |  | SHUTDOWN |  | IPS-M-PM-290 SECTION 6.8.
LUBRICATING OIL PRESSURE | [11 empty] | Remark: |  | P&ID For Fire Water Network
FUEL PRESSURE | [11 empty] | (No.BK-GCS-PEDCO-120-SA-PI-0001.)
ENGINE OIL TEMPERATURE | [11 empty] | shall be followed.
FUEL TEMPERATURE
OVER SPEED
DIFF PRESS SWITCH ON FILTER
MANOMETER ON OIL CIRCUIT;
DOWNSTREAM OF PUMP
DOWNSTREAM OF FILTER
SIGHT GLASSES ON OIL CIRCUIT

## Diesel(4)
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
شماره پیمان: |  | MECHANICAL DATA SHEETS FOR FIRE WATER PUMPS-DIESEL ENGINE DRIVEN | [7 empty] | شماره صفحه: 13 از 13
053-073-9184 |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  | BK | GCS | PEDCO | 120 | ME | DT | 0030 | D03
Diesel Engine Data Sheet For Fire Water Pump - P-2301 B (SI UNIT) (4 of 4)
ENGINE EXHAUST TURBOCHARGER
|  |  |  | TE BEFORE/ |  |  | PI BEFORE/
|  |  |  | AFTER COOLER |  |  | AFTER COOLER
CIRCUIT OF:
RAW WATER |  |  |  |  | / |  |  | /
FRESH WATER |  |  |  |  | / |  |  | /
OIL |  |  |  |  | / |  |  | /
SUPERCHARGING:
AIRSIDE |  |  |  |  | / |  |  | /
WATERSIDE |  |  |  |  | / |  |  | /
REMARKS:
For each pump set one 400V, 3PH/N auxiliary feeder is delivered by purchaser.
All required power for local control panel ( 230VAC/110VAC/24VDC) shall be convert by vendor as request.