## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0029_D03 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1342 |  |  | Transmital Date: 30/Aug/2022
Document Title: Mechanical Data Sheets For Fire Water Main Pump-Elect.Motor Driven |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-ME-TR-1342 |  |  | Transmital Date: 30/Aug/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-ME-DT-0029_D02 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Mechanical Comments:
1 | This document is approved by considering below Notes: |  | BK-SUR-ENG-MEC-01-05823 | 2022-10-03
2 | , the below items shall be clarified in TCL by vendor 1-Nss: 213 shall be considered and clarified by Vendor 2-By considering material I-2, the flange shall be FF 4-Hydrotest pressure shall not be less than 17.24 as per NFPA20 |  | BK-SUR-ENG-MEC-01-05823 | 2022-10-03 | 1- Not accepted, this requirement has not been mentioned in project specification and related standards. This issue will be clarified in vendor's offer stage and TCL. 2- Noted 3- Noted, Will be added as note.
Electrical comments:
1 | در نوت شماره 11 گفته شده توان موتور بايستي 150 درصد مقدار مورد نياز در نظر گرفته شود. توان هيدروليكي پمپ در ديتا شيت ارسالي برابر 125 كيلو وات قيد شده چنانچه اين توان با احتساب 150 درصد توان هيدروليكي مورد نياز محاسبه شده است موتور 300 كيلوواتي در نظر گرفته شده در مدارك برقي مناسب است در غير اينصورت توان موتور در مدارك برقي بايستي بازنگري شود وبه حدود 400 كيلو وات افزايش داده شود و يا اين نوت چنانچه مبناي قراردادي ندارد حذف گردد. |  | BK-SUR-ENG-MEC-01-05823 | 2022-10-03 | نوت شماره 11 مطابق استانداردهای NFPA 20 و IPS-M-PM-125 بوده و سازنده ملزم به پیروی از آن است. توان هیدرولیکی پمپ بدون احتساب 150 درصد بوده و سازنده می بایست پمپ را برای 150 درصد ظرفیت Rated انتخاب کند. پیرو مذاکره صورت گرفته با بخش برق این مشاور، مقرر گردید بعد از دریافت پیشنهادات فنی سازندگان و نهایی شدن توان پمپ و موتور، این مورد در مدارک بخش برق اصلاح و نهایی شود.
2 | با توجه به وجود ابهام مطرح شده در كامنت قبلي لازم است مشاور توان الكتروموتور را محاسبه و در ديتا شيت ذكر نمايد. بديهي است اين مقدار بعدا توسط سازنده نهايي خواهد شد. |  | BK-SUR-ENG-MEC-01-05823 | 2022-10-03 | با توجه به توان هیدرولیکی 129.5 کیلووات و در نظر گرفتن 65 درصد راندمان، توان تخمینی مورد نیاز پمپ 199.2 کیلووات خواهد بود که بصورت نوت در مدرک مکانیکال دیتاشیت اضافه می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: H. Adineh | Signature | M. Fakharian
| Date: 10/03/2022 |  |  |  |  | Date: 10/18/2022