## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-DT-0006_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1348 |  |  | Transmital Date: 3 Sep 2022
Document Title: Data Sheets For Control/Regulator valves - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1084 |  |  | Transmital Date: 3 Sep 2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-IN-DT-0006_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق بند 13 شرايط عمومي پيمان في مابين و با توجه به مسئوليتهاي كامل مالي/قراردادي پيمانكار, مسئوليت بروز هرگونه اشتباه و تناقض, كمبود اسناد و مدارك فني و اطلاعات تهيه شده توسط پيمانكار, اعم از اينكه از سوي كارفرما تاييد شده يا نشده باشد, به عهده پيمانكار فرعي (هيرگان) مي باشد. |  | BK-SUR-ENG-INS-01-05712 | 2022-09-18 | ملاحظه شد.
2 | با توجه به اينكه مدارك مرجع و مرتبط داراي كامنت مي باشد و نهايي نيستند هر گونه تغييري بايد در اين مدرك نيز منعكس شود. |  | BK-SUR-ENG-INS-01-05712 | 2022-09-18 | ملاحظه شد.
3 | با توجه به كامنت شماره 7 مدرك پيشين براي Trace راحت تر مدرك، نسخه مدارك مرجع درج گردد. |  | BK-SUR-ENG-INS-01-05712 | 2022-09-18 | مطابق توافقات نسخه مدرک P&ID درج گردید.
4 | با توجه به محاسبات CV، فيلدهاي مرتبط تكميل گردد و تاييد وندور (VTC) درج گردد |  | BK-SUR-ENG-INS-01-05712 | 2022-09-18 | مطابق توافقات اعمال شد.
5 | سطر 29، ذكر گردد كه موارد Rating مطابق مدرك PMS مي باشد. |  | BK-SUR-ENG-INS-01-05712 | 2022-09-18 | مطابق توافقات اعمال شد.
6 | Facing مطابق PMS ذكر گردد. |  | BK-SUR-ENG-INS-01-05712 | 2022-09-18 | مطابق توافقات اعمال شد.
7 | متريال Trim اصلاح شود. مطابق مدرك PMS پروژه Trim شير در كلاس FN05 بايستي Trim No.12 يعني SS316 and Hardfaced باشد. |  | BK-SUR-ENG-INS-01-05712 | 2022-09-18 | مطابق توافقات اعمال شد.
8 | Seat Material اصلاح شود: 18Cr-8Ni-Mo |  | BK-SUR-ENG-INS-01-05712 | 2022-09-18 | متریال بالاتر مطابق توافقات درج گردید.
9 | نوت شماره 4 اصلاح شود: Trim part material shall be considered as minimum 316SS and Hardfaced or any equal hard steel. |  | BK-SUR-ENG-INS-01-05712 | 2022-09-18 | مطابق توافقات اعمال شد.
10 | كامنت هاي بخش فرآيند متعاقبا اعلام مي گردد. |  | BK-SUR-ENG-INS-01-05712 | 2022-09-18 | ملاحظه شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 18 Sep 2022 |  |  |  |  | Date: