## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-CV-DW-0006 |  |  |  |  | EPC Contractor Tr. No. : BK-HD-PEDCO-T-1312 |  |  | Transmital Date: 24-AGU-2022
Document Title : Standard Drawing For Catch Basins |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0006-CV-T-1312 |  |  | Transmital Date: 24-AGU-2022
[5 empty] | CRS No: NISOC-CRS-BK-GNRAL-PEDCO-000-CV-DW-0006-D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در ELEV1. و دیگر صفحات درصد تراکم خاک کوبیده به 95 درصد اصلاح گردد. این موضوع قبلا نیز به اطلاع پیمانکار رسید لکن لحاظ نگردید. بازنگری و اصلاح شود. |  | 1401-2294-210047 | 1401/06/13 | اعمال شد
2 | در بخش CATCH BASIN FOR ALL AREAS متن TOP MANHOLE LEVEL اصلاح شود. |  | 1401-2294-210047 | 1401/06/13 | اعمال شد
3 | مرجع جدول SIPHON PIPE SEAL در NOTE نقشه درج گردد. |  | 1401-2294-210047 | 1401/06/13 | این جدول براساس روابط هندسی و زاویه ورود و قطر لوله حساب شده است، همچنین رفرنس NIOEC-SD-1006-10/10-A3 نیز در فهرست مدارک قرار داده شد.
4 | استفاده از CEMENT MORTAR GROUT برای آببند شدن سازه مورد تایید نمی باشد. مقتضی است به مصالح SELANT غیر حلال نفتی اشاره شود. |  | 1401-2294-210047 | 1401/06/13 | برای آب بند کردن فضای بین لوله ها و بدنه بتنی از گروت پایه سیمانی استفاده شده است که مانند بتن خاصیت مقاوم در برابر ترکیبات هیدروکربنی دارد و غیر حلال نفتی می باشد.
5 | در صفحه 2 بخش OPENING DETAIL متریال STEEL PLATE و ANCHOR PLATE در نقشه ها به طور کامل نمایش داده نشده است، در هر دو تصویر ترسیم گردند. |  | 1401-2294-210047 | 1401/06/13 | اعمال شد
6 | برای بدنه بتنی درگیر با خاک، در NOTES به عبارت USE WATER PROOF PRIMER MATERIAL اشاره گردد. |  | 1401-2294-210047 | 1401/06/13 | برای حفاظت بدنه بتنی درگیر با خاک به SATANDARD DETAIL OF MISCELLANEOUS به شماره مدرک BK-GNRAL-PEDCO-000-CV-DW-0040 اشاره شد که در دیتیل CONCRETE PROTECTION شیت 2 به این موضوع پرداخته است ، همچنین رفرنس مذکور در NOTES نیز اضافه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: