## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-SL-0002_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1380 |  |  | Transmital Date: 07-Sep-2022
Document Title: UPS Single Line Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0106-EL-TR-1380 |  |  | Transmital Date: 07-Sep-2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-EL-SL-0002_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | ارت بدنه دستگاه UPS می بایست 70 در نظر گرفته شود. |  | 1401-2294-229895 | 1401-06-28 | اعمال گردید.
2 | تابلوهای توزیع بارهای سیستم در مدرک نمایش داده شود. در این خصوص لازم است با هماهنگی بخش ابزاردقیق بارهای خروجی در مدرک لحاظ گردند. در صورت redundant بودن پاور سیستم های کنترل لازم است که جهت هر سیستم دو عدد کلید با جریان مناسب در نظر گرفته شود. همچنین جهت بارهای موجود واحد نیز دو عدد کلید خروجی با توان یک و نیم کیلووات لحاظ گردد. |  | 1401-2294-229895 | 1401-06-28 | خروجی های توزیع مورد نیاز سیستم ابزاردقیق به همراه Redundant در ویرایش قبل نیز نشان داده شده است. با این حال در صورت تغییر خروجی های ابزاردقیق، تغییرات در ویرایش های بعدی لحاظ خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 21-Sep-22 |  |  |  |  | Date: