## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-SL-0002_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1380 |  |  | Transmital Date: 07-Sep-2022
Document Title: UPS Single Line Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0106-EL-TR-1380 |  |  | Transmital Date: 07-Sep-2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-EL-SL-0002_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on Calculation Note For UPS System. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | مدرک محاسباتی UPS بر اساس بارهای اعلامی بخش ابزاردقیق ویرایش شده است. همچنین فیدرهای این مدرک مطابق با فیدرهای لیست بار ابزادرقیق می باشد. در صورت هرگونه نغییر در مدرک محاسباتی، این مدرک بازنگری خواهد شد. |  |  | See below item 9
2 | According to our telephone conversation, a separate sheet shall be added and 110AC distribution borad with all related feeders including incoming and outgoing feeders shall be shown. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | مطابق با بارهای ارائه شده در ترنسمیتال 852 که مربوط بعه بخش ابزاردقیق می باشد، خروجی ها در نظر گرفته شده است. |  |  | Noted and Closed.
3 | Following items shall be added as notes: - Interlocks will be provided to inhibit battery boost charge if battery room ventilation is out of service. -Automatic battery isolation facility shall be provided for incoming MCCB of battery bank. incoming MCCB of battery bank shall be open when F&G system send battery insulation signal to the UPS. -An earth fault monitoring shall be considered for every 10 feeders for easy of finding faulty branch. -Metering and protection system shall be completed based on ac ups specification and detailed information shall be indicated On vendor drawing. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | موارد مطروحه در مدرک اضافه گردید. |  |  | Noted and Closed.
4 | Some technical characteristics of equipment shall be added and specified on single line diagram such as rated voltage/short circuit level/rated current of 110AC distribution board, capacity/back up time/number and type of battery. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | این مدرک بر اساس مدرک ارسالی کارفرما در نامه شماره 375310 به روزرسانی شده است. علاوه بر این در نوت شماره 8 اشاره شده است که سازنده موظف به تعیین دقیق ظرفیت تجهیزات می باشد. |  |  | Noted and Closed.
5 | The body of panels shall be earthed directly from two point. It shall be shown. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | علاوه بر اینکه ارت بدنه و تابلوی Distribution در مدرک نشان داده شده است، نوت شماره 13 نیز به این موضوع اشاره دارد. |  |  | Noted and Closed.
6 | According to our telephone conversation, related note for cable size, type and tag shall be added. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | نوت شماره 6 به این موضوع اختصاص داده شده است. |  |  | Noted and Closed.
7 | Battery limit of fuse box and battery bank and cable between them shall be shown. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | این مدرک بر اساس مدرک ارسالی کارفرما در نامه شماره 375310 به روزرسانی شده است. |  |  | Noted and Closed.
8 | According to meeting date 1400.12.22 at PEDCO office, regarding to control system will be considered redundancy, so for each control system shall be considered two feeders instead of one feeder. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | این مدرک بر اساس مدرک ارسالی کارفرما در نامه شماره 375310 به روزرسانی شده است. |  |  | Noted and Closed.
9 | See above item 1: According to NISOC letter No. 01/2294/31452 date 1401/01/30 (Response to Tr-737), this document shall be revised base on commnets on DC charger calculation. |  | BK-SUR-ENG-ELE-01-05739 | 2022-09-21 | مدرک محاسباتی UPS بر اساس بارهای اعلامی بخش ابزاردقیق ویرایش شده است. همچنین فیدرهای این مدرک مطابق با فیدرهای لیست بار ابزادرقیق می باشد. در صورت هرگونه نغییر در مدرک محاسباتی، این مدرک بازنگری خواهد شد.
10 | It is recommended the the related convereter feeder fed from 110DC bus (between battery and inverter) this shall be finalized by UPS Manufacturer. |  | BK-SUR-ENG-ELE-01-05739 | 2022-09-21 | نوت شماره 16 اضافه گردید. در صورتیکه بتوان از لینک دی سی برای تأمین برق 24 ولت سیستم کنترل موجود استفاده کرد، به جای مبدل AC به DC از مبدل DC به DC استفاده خواهد شد. در اینصورت نوت شماره 15 دیگر معتبر نخواهد بود.
11 | The body of panel shall be earthed by 70mm² instead of 35mm². |  | BK-SUR-ENG-ELE-01-05739 | 2022-09-21 | اعمال گردید.
12 | Following item shall be added as notes: -Interlocks will be provided to active battery room ventilation when UPS is on battery boost charge mode. |  | BK-SUR-ENG-ELE-01-05739 | 2022-09-21 | نوت شماره 9 بر هیمن موضوع دلالت دارد.
13 | RCBO shall be used instead of MCB for socket feeders. |  | BK-SUR-ENG-ELE-01-05739 | 2022-09-21 | اعمال گردید
14 | It shall be clarify the 24VDC distribution panel diagram has been shown in diagram base on which reference document. Meanwhile this document shall not be revised before client approval. |  | BK-SUR-ENG-ELE-01-05739 | 2022-09-21 | تابلوی توزیع آن حذف گردید.
15 | Regarding to available options for feeding existing marshaling system and FACP, this document shall not be reissued till finalizing best scenario by Instrument. At the other hand feeding existing marshaling cabint from new UPS is not in the scope of project work. |  | BK-SUR-ENG-ELE-01-05739 | 2022-09-21 | این دیاگرام تک خطی بر اساس صورتجلسه در دفتر آن مدیریت محترم ویرایش گردیده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 21-Sep-22 |  |  |  |  | Date: