## TBE for PG
نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني مربوط به موقعیت W008N
Contract No: 9184 – 073 - 053 |  |  | TBE For Presssure Gauge
|  |  | Project Code |  | Package | Company code |  | Scope | Disc Code | Doc. Code | Sequence No. | Rev. Code
|  |  | BK |  | W008N | PEDCO |  | 110 | IN | TB | 0002 | D01
REQ. NAME : |  | MR for Pressure Gauge |  | BIDDER:
REQ. NO. : |  | RR-00-PS-110-IN-MR-0030 |  | NAME: |  |  | سنگان صنعت |  |  | تجهیزات فراصنعت آرمان |  | ساعی سامانگر صنعت سبز (4S)
REQ. REV. : |  | D03 |  | QUOTATION NO.: |  |  | 1400-P-8716 |  |  | 850ف ب 1401 |  | 140107012
EQUIPMENT TYPE : |  | Pressure Gauge |  | QUOTATION DATE: |  |  | 2022-03-13 |  |  | 1401-07-12 |  | 1401-07-27
NO. | DESCRIPTION |  |  | REFERENCE / SPECIFIED
[7 empty] | A |  |  | B |  | C
A | Scope of Work And Supply
1 | Tag Number |  |  | PG-1101, PG-1102
2 | Scope of Work And Supply |  |  | Pressure Gauge |  |  | Confirmed by Vendor |  |  | Confirmed by Vendor |  | Confirmed by Vendor
3 | Delivary Date |  |  | B.V. |  |  | 90 working Days after advanced payment and approved technical documents |  |  | Not Specified |  | 120 days after down payment.
4 | Delivary Place |  |  | Ex.Work |  |  | EX-work .sangan sanat (Tehran) |  |  | Not Specified |  | DDP
5 | Bid Validity Period |  |  | B.V. |  |  | 30 days |  |  | Not Specified |  | 30 Days.
6 | GUARANTEE |  |  | Requisition eighteen (18) months from the date of the Installation and Commissioning or twenty-four (24) months after the date of delivery of materials (whichever comes earlier) |  |  | Confirmed by Vendor |  |  | Confirmed by Vendor (12 Month Guarantee as per proposal) |  | 24 Month after shipment 18 Month after Installation
7 | MANUFACTURER (VENDOR LIST) |  |  | AVL |  |  | Confirmed by Vendor |  |  | Confirmed |  | Confirmed by Vendor
8 | SPARE PARTS |  |  | 5% complete set (3 Set PG & 1 Set TG for all wells) |  |  | Submitted |  |  | Submitted |  | As number of quotation is only 1 for all items
B | Technical Requirements
1 | Environmental / Process Condition |  |  | According to data sheet |  |  | Confirmed by Vendor (Gauges accuracies will be effected by this tempreture and they should be protected by sunshade) |  |  | Confirmed by Vendor (Gauges accuracies will be effected by this tempreture and they should be protected by sunshade) |  | Gauges accuracies will be effected by this tempreture and they should be protected by sunshade
2 | Pressure Element Type |  |  | Bourdon |  |  | Bourdon |  |  | Bourdon |  | Bourdon | confirmed
3 | Pressure Element Material |  |  | Stainless Steel 316 |  |  | Stainless Steel 316 |  |  | Stainless Steel 316 |  | Stainless Steel 316 | confirmed
4 | Calibration Range |  |  | As requested |  |  | As per data sheet |  |  | As per data sheet |  | confirmed by Vendor (Not as per data sheet for one tag no.) | confirmed
5 | Eng. Unit |  |  | Bar/Psi |  |  | Yes |  |  | Yes |  | Confirmed by Vendor
6 | Zero Adjustment |  |  | Yes |  |  | Yes |  |  | Yes |  | Confirmed by Vendor
7 | Mounting |  |  | As requested |  |  | Confirmed by Vendor |  |  | Direct- Bottom |  | Yes | confirmed
8 | Ring Construction/Material |  |  | Screwed/ Stainless Steel |  |  | Confirmed by Vendor |  |  | Not Specified |  | Yes | confirmed
9 | Dial Size |  |  | 150mm (Black graduation on white background) |  |  | Yes |  |  | Yes |  | Yes | Confirmed
10 | Case Material |  |  | Stainless Steel 304 |  |  | Yes |  |  | Yes |  | Yes | Confirmed
11 | Socket Material |  |  | Stainless Steel 316 |  |  | Confirmed by Vendor |  |  | Not Specified |  | SS 316L | Confirmed
12 | Connection Size |  |  | 1/2" NPTM |  |  | Yes |  |  | Yes |  | Yes | Confirmed
13 | Movement Material |  |  | 316 S.S. |  |  | 304 S.S. |  |  | SS 316 |  | SS
14 | Accuracy |  |  | ±0.6% Full Scale |  |  | According To BS 1780 ,±0.5% FSD |  |  | ±0.6% of F.S |  | 0.6% FS
15 | Over range Protection |  |  | 30% Full Scale |  |  | 1.3 of F.S |  |  | Yes |  | Yes
16 | Weather Protection |  |  | IP65 |  |  | IP65 |  |  | IP 65 |  | IP 65
17 | Blow-Out Protection |  |  | Back, Disc |  |  | Back blow out including baffle wall |  |  | Yes |  | Confirmed by Vendor
18 | Shatter proof & soild front |  |  | Yes |  |  | Confirmed by Vendor |  |  | Soild front |  | Confirmed by Vendor
19 | Pressure valve protector |  |  | Yes |  |  | Yes |  |  | Yes |  | Confirmed by Vendor
20 | Oil Filled Case |  |  | Yes |  |  | Silicon |  |  | Silicon oil filled |  | Confirmed by Vendor
21 | Manifold type for non-diaphragm seal items |  |  | 2 Valves |  |  | Yes |  |  | 2-valve manifold |  | Yes | Confirmed
22 | Manifold Material |  |  | Stainless Steel 316 |  |  | Stainless Steel 316 |  |  | Stainless Steel 316 |  | SS 316 | Confirmed
23 | Manifold Connection (Instrument/Process) |  |  | 1/2"NPTF |  |  | 1/2" NPT- F |  |  | 1/2"NPT |  | 1/2" NPT- F
24 | In Compliance with NACE Std. |  |  | As requested |  |  | Yes |  |  | Yes |  | Yes | Confirmed
25 | Manifold Vent/Drain Size & Rating |  |  | 1/4" NPTF & 3000 psi |  |  | Confirmed by Vendor |  |  | Yes |  | Confirmed by Vendor
26 | SS Name Plate |  |  | As requested |  |  | Confirmed by Vendor |  |  | Confirmed by Vendor |  | Confirmed by Vendor
C | Test and Inspection
1 | Test and Inspection | [5 empty] | Submitted |  |  | Not Submitted |  | Confirmed to Submit
D | Document Requirements
1 | Country Of Origin |  |  | Contract |  |  | IRAN |  |  | IRAN |  | IRAN
2 | Material Test / Calibration Certificate |  |  | Requisition |  |  | LAB. Result |  |  | Confirmed by Vendor |  | Will be submmited during manufacturing process
3 | Level of Similar Experience in past 10 years |  |  | Vendor 's Quotation |  |  | Refrence list is attached |  |  | Not Submitted |  | Confirmed to Submit
F | Deviations / Alternatives
1 | Deviations (if any) |  |  | signed and stamped |  |  | Submitted |  |  | Not Submitted |  | Not Submitted
2 | Manufacturer's Location |  |  | - |  |  | Tehran - Qom highway -IRAN |  |  | Esfahan-IRAN |  | IRAN
H | PROPOSAL DOCUMENTATION
1 | Quality plan / ITP |  |  | shall be submitted |  |  | Attached |  |  | Not Submitted |  | Not Submitted
2 | Standard certificates |  |  | shall be submitted |  |  | Confirmed by Vendor |  |  | Confirmed to submit |  | Will be submitted after PO
3 | Confirmed scope of work & scope of supply as per MR |  |  | shall be submitted |  |  | Confirmed by Vendor |  |  | Confirmed by Vendor |  | Confirmed by vendor
4 | Filled TBE |  |  | shall be submitted |  |  | Submitted |  |  | Not Submitted |  | Submitted
5 | Summary sheets |  |  | shall be submitted |  |  | Submitted |  |  | Not Submitted |  | Confirmed to Submit
7 | Reference list |  |  | shall be submitted |  |  | Submitted |  |  | Not Submitted |  | Confirmed to Submit
8 | Catalouges |  |  | shall be submitted |  |  | Submitted |  |  | Not Submitted |  | Confirmed to Submit
9 | Datasheet/ Drawing |  |  | shall be submitted |  |  | After PO |  |  | After PO |  | After PO
10 | Order code (Part No.) |  |  | shall be submitted |  |  | Model number is mentioned in quotation. |  |  | Not Submitted |  | Before Manufacturing | Submitted
GENERAL ACCEPTANCE FOR QUOTATION: | [6 empty] | ACCEPTED |  |  | ACCEPTED |  | ACCEPTED
Notes:
A : ACCEPTABLE (TECHNICALLY MEETS REQUIREMENT)
NA: NOT ACCEPTABLE (TECHNICALLY DOES NOT MEET REQUIREMENT)
CA: CONDITIONALLY ACCEPTED
INA: INFORMATION NOT AVAILABLE
N/A: NOT APPLICABLE
D01