## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W018S-PEDCO-110-IN-TB-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1012 |  |  | Transmital Date: 28 May 2022
Document Title: TBE/TBA For Field Instrumentations - W018S |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-1012 |  |  | Transmital Date: 28 May 2022
[5 empty] | CRS No: NISOC-CRS-BK-W018S-PEDCO-110-IN-TB-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | 1- مطابق SPEC دقت برای گیج فشار 0.5% F.S. در نظر گرفته شود. |  | 01/2294/111541 | 1401/03/31 | مطابق با بند 4.1.1.2 IPS-M-IN-110 ، دقت گیج ها برابر 0.6% F.S. در نظر گرفته شده است.
2 | 2- طراحی گیج های دما و فشار بدون سایه باشد. |  | 01/2294/111541 | 1401/03/31 | مدرک مطابق با فرمت تایید شده TBE تهیه گردیده و به روز رسانی شده است.
3 | 3- قطعات یدکی برای تجهیزات در نظر گرفته شود. |  | 01/2294/111541 | 1401/03/31 | Deviation List از تمامی سازندگان درخواست گردیده است. در صورت عدم ارائه این مورد در جدول TBE ذکر گردیده است.
4 | 4- از چهار شرکت (آسیا ابزاردقیق-پارس جهد-ساعی سامانگر صنعت سبز-سنگان صنعت) فقط یک شرکت محصول گیج فشار و گیج دما را مطابق لیست بلند وزارت نفت تامین/تولید می کند. لذا جدول ارزیابی قابل قبول نبوده و مدرک عودت می گردد. |  | 01/2294/111541 | 1401/03/31 | سازندگان پیشنهادی در این نسخه از TBE ارائه شده همگی در لیست بلند نفت می باشند.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 12 Sep 2022 |  |  |  |  | Date: