## TBE for PG
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
TBE/TBA FOR FIELD INSTRUMENT
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | XXXX | PEDCO |  | 110 | IN | TB |  | 0002 | D00
REQ. NAME : |  | PMR For Field Instrumentations | BIDDER: |  |  |  | SANGAN SANAT
REQ. NO. : |  | BK-XXXX-PEDCO-110-IN-MR-0002 | NAME:
REQ. REV. : |  | D03 | QUOTATION NO.: |  |  |  | 1400-P-8716
EQUIPMENT TYPE : |  | Pressure Gauge | QUOTATION DATE: |  |  |  | 13-March-2022
NO. | DESCRIPTION |  | REFERENCE / SPECIFIED
[7 empty] | A |  |  |  | B |  |  | C | D
A | Scope of Work And Supply
1 | Reference documents for proposal (MR, spec, datasheet & etc) |  | According to the last revision |  |  |  | confirmed
2 | Scope of Work And Supply |  | Pressure Gauge |  |  |  | confirmed
3 | Delivary Date |  | B.V. |  |  |  | 90 working Days after advanced payment and approved technical documents
4 | Delivary Place |  | Ex.Work |  |  |  | EX.WORKS
5 | Bid Validity Period |  | B.V. |  |  |  | 30 days
6 | GUARANTEE & WARRANTY |  | Requisition The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the installation date of each equipment/packages at site, also the VENDOR shall be able to provide spares back up and support for the plant life of at least 20 years. |  |  |  | confirmed
7 | MANUFACTURER (VENDOR LIST) |  | AVL |  |  |  | SANGAN SANAT
8 | SPARE PARTS |  | 10% Of Each Type & Range(Min 1 No) |  |  |  | confirmed
B | Technical Requirements
1 | Environmental Condition |  | • Minimum ambient temperature (°C): -5 °C • Maximum steel surface exposed to sun (°C): 85 °C |  |  |  | confirmed
2 | Process Condition |  | As requested |  |  |  | confirmed
3 | Pressure Element Type |  | Bourdon |  |  |  | confirmed
4 | Pressure Element Material |  | Stainless Steel 316 |  |  |  | confirmed
5 | Calibration Range |  | As requested |  |  |  | confirmed
6 | Eng. Unit |  | Bar/Psi |  |  |  | confirmed
7 | Zero Adjustment |  | Yes |  |  |  | confirmed
8 | Mounting |  | As requested |  |  |  | confirmed
9 | Ring Construction/Material |  | Screwed/ Stainless Steel |  |  |  | confirmed
10 | Dial Size |  | 150mm (Black graduation on white background) |  |  |  | confirmed
11 | Case Material |  | stainless steel 304 |  |  |  | confirmed
12 | Socket Material |  | Stainless Steel 316 |  |  |  | confirmed
13 | Process Connection Size |  | 1/2" NPTM |  |  |  | confirmed
14 | Movement Material |  | 316 S.S. |  |  |  | 304 S.S. mentioned in datasheet
15 | Accuracy |  | ±5% of F.S. |  |  |  | 0.5 % is available.
16 | Over range Protection |  | 30% Full Scale |  |  |  | confirmed
17 | Weather Protection |  | IP65 |  |  |  | confirmed
18 | Blow-Out Protection |  | Back, Disc |  |  |  | confirmed
19 | Safety glass(shatter proof) & soild front |  | Yes |  |  |  | confirmed
20 | Pressure valve protector |  | As requested |  |  |  | confirmed
21 | Oil Filled Case |  | Yes |  |  |  | confirmed
22 | Manifold type for non-diaphragm seal items |  | 2 Valves |  |  |  | confirmed
23 | Manifold Material |  | Stainless Steel 316 |  |  |  | confirmed
24 | Manifold Connection (Instrument/Process) |  | 1/2"NPTF |  |  |  | confirmed
25 | In Complaince with Nace Standard |  | As requested |  |  |  | confirmed
26 | Manifold Vent/Drain Size & Rating |  | 1/4" NPTF & 3000 psi |  |  |  | confirmed
27 | SS Name Plate |  | As requested |  |  |  | confirmed
28 | Painting |  | Vendor 's Standard |  |  |  | N/A
C | Test and Inspection
1 | Test and Inspection |  | Project IDS, Requisition |  |  |  | confirmed
D | Document Requirements
1 | Document List |  | Requisition |  |  |  | VPIS list, datasheet, drowing , ITP,Installation& Operation Manual , final data book
2 | Country Of Origin |  | Contract |  |  |  | made in iran
3 | Material Test / Calibration Certificate |  | Requisition |  |  |  | LAB. Result
E | Level of Similar Experience in past 10 years |  | Vendor 's Quotation |  |  |  | refrence list is attached
F | Deviations / Alternatives
1 | Deviations (if any) |  | signed and stamped
G | Manufacturer's Location |  | - |  |  |  | No.16,10th Golshan St.Golestan Blv.Shamsabab industrial zone, Tehran - Qom highway
H | PROPOSAL DOCUMENTATION
1 | Quality plan / ITP |  | shall be submitted |  |  |  | is attached.
2 | Standard certificates |  | shall be submitted |  |  |  | confirmed
3 | Confirmed scope of work & scope of supply as per MR |  | shall be submitted |  |  |  | confirmed
4 | Filled TBE |  | shall be submitted |  |  |  | confirmed
5 | Summary sheets |  | shall be submitted |  |  |  | is attached.
6 | Reference list |  | shall be submitted |  |  |  | is attached.
7 | Catalouges |  | shall be submitted |  |  |  | is attached.
8 | Datasheet/ Drawing |  | shall be submitted |  |  |  | is attached.
9 | Order code (Part No.) |  | shall be submitted |  |  |  | model number is mentioned in quotation.
General Technical acceptance of Quotation
Notes:
- Each items to be specified or confirmed by vendor, deviation to be colored red.

## TBE for TG
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
TBE/TBA FOR FIELD INSTRUMENT
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | XXXX | PEDCO |  | 110 | IN | TB |  | 0002 | D00
REQ. NAME : |  | PMR For Field Instrumentations | BIDDER: |  |  |  | SANGAN SANAT
REQ. NO. : |  | BK-XXXX-PEDCO-110-IN-MR-0002 | NAME:
REQ. REV. : |  | D00 | QUOTATION NO.: |  |  |  | 1400-P-8717
EQUIPMENT TYPE : |  | Temperature Gauges & Thermowell | QUOTATION DATE: |  |  |  | 13-March-2022
NO. | DESCRIPTION |  | REFERENCE / SPECIFIED
[7 empty] | A |  |  |  | B |  |  | C | D
A | Scope of Work And Supply
1 | Reference documents for proposal (MR, spec, datasheet & etc) |  | According to the last revision |  |  |  | confirmed
2 | Scope of Work And Supply |  | Temperature Gauges |  |  |  | confirmed
3 | Delivary Date |  | B.V. |  |  |  | 90 working Days after advanced payment and approved technical documents
4 | Delivary Place |  | Ex.Work |  |  |  | EX.WORKS
5 | Bid Validity Period |  | B.V. |  |  |  | 30 days
6 | GUARANTEE & WARRANTY |  | Requisition The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the installation date of each equipment/packages at site, also the VENDOR shall be able to provide spares back up and support for the plant life of at least 20 years. |  |  |  | confirmed
7 | MANUFACTURER (VENDOR LIST) |  | AVL |  |  |  | SANGAN SANAT
8 | SPARE PARTS |  | 10% Of Each Type & Range(Min 1 No) (Temperature Gauge + Thermowell) |  |  |  | confirmed
B | Technical Requirements
1 | Environmental Condition |  | • Minimum ambient temperature (°C): -5 °C • Maximum steel surface exposed to sun (°C): 85 °C |  |  |  | confirmed
2 | Process Condition |  | As requested |  |  |  | confirmed
3 | Thermometer Type |  | Bimetal / Filled type (As requested) |  |  |  | confirmed
4 | Calibrated Range |  | As requested |  |  |  | According to data sheet
5 | Dial Size |  | 150 mm |  |  |  | confirmed
6 | Dial Color |  | White with black Letter |  |  |  | confirmed
7 | Case Material |  | Stainless Steel 304 |  |  |  | confirmed
8 | Process Connection Size/ rating |  | 1 1/2 RTJ,/ API 3000 |  |  |  | confirmed
9 | Eng. Unit |  | °C/ °F |  |  |  | confirmed
10 | Accuracy |  | Better than ± 1% of full span |  |  |  | confirmed
11 | Pointer Color / Material |  | Black / Metallic |  |  |  | confirmed
12 | Stem Type / Material |  | Threaded / 316 SS |  |  |  | confirmed
13 | Stem Diameter |  | 6 mm |  |  |  | confirmed
14 | Ingress Protection |  | IP 65 |  |  |  | confirmed
15 | Window Material |  | Shatterproof Glass |  |  |  | safety glass
16 | Zero Adjustment |  | Pointer |  |  |  | confirmed
17 | Over range Protection |  | 1.5 times the maximum scale. |  |  |  | confirmed
18 | Connection (Back or Bottom) |  | Every Angle |  |  |  | confirm ( back)
19 | External Calibration Adjustment |  | Required |  |  |  | confirmed
20 | Head Type |  | Oriantable Head |  |  |  | confirmed
21 | Bulb Material |  | SS 316 |  |  |  | confirmed
22 | Thermowell |  | Tapered Drilled Bar Stock |  |  |  | confirmed
23 | Well conn. & Flange Material |  | As requested & Stainless Steel 316 |  |  |  | confirmed
24 | Thermowell Connection |  | As requested |  |  |  | according to datasheet
25 | In Complaince with Nace Standard |  | As requested |  |  |  | according to datasheet
26 | Insertion Length (U) mm |  | As requested |  |  |  | According to data sheet
27 | SS Name Plate |  | As requested |  |  |  | confirmed
28 | Accessories for installation for remote type |  | As requested |  |  |  | N/A
C | Test and Inspection
1 | Test and Inspection |  | Project IDS, Requisition |  |  |  | confirmed
D | Document Requirements
1 | Document List |  | Requisition |  |  |  | VPIS list, datasheet, drowing , ITP,Installation& Operation Manual final data book
2 | Country Of Origin Of Material |  | Contract |  |  |  | made in iran
3 | Wake Frequency Calculaton |  | Requisition |  |  |  | NO Needed. Velocity is 0
4 | Material Test Certificate |  | Requisition |  |  |  | LAB. Result
E | Level of Similar Experience in past 10 years |  | Vendor 's Quotation |  |  |  | refrence list is attached
F | Deviations / Alternatives
1 | Deviations (if any) |  | signed and stamped |  |  |  | is attached.
G | Manufacturer's Location |  | - |  |  |  | No.16,10th Golshan St.Golestan Blv.Shamsabab industrial zone, Tehran - Qom highway
H | PROPOSAL DOCUMENTATION
1 | Quality plan / ITP |  | shall be submitted |  |  |  | is attached.
2 | Standard certificates |  | shall be submitted |  |  |  | is attached.
3 | Confirmed scope of work & scope of supply as per MR |  | shall be submitted |  |  |  | as per MR
4 | Filled TBA |  | shall be submitted |  |  |  | confirmed
5 | Summary sheets |  | shall be submitted |  |  |  | is attached.
6 | Reference list |  | shall be submitted |  |  |  | is attached.
7 | Catalouges |  | shall be submitted |  |  |  | is attached.
8 | Datasheet/ Drawing |  | shall be submitted |  |  |  | is attached.
9 | Order code (Part No.) |  | shall be submitted |  |  |  | model number is mentioned in quotation.
General Technical acceptance of Quotation
Notes:
- Each items to be specified or confirmed by vendor, deviation to be colored red.