## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-DT-0004_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1284 |  |  | Transmital Date: 17-Aug-2022
Document Title: Data Sheets For Diesel Generator of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0105-EL-TR-1284 |  |  | Transmital Date: 17-Aug-2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-EL-DT-0004_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بند 2.22. تعداد دو عدد درج شده در این ردیف صحیح نمی باشد. مقدار صحیح با توجه به نوع باتری های (نیکل کادمیوم) 20 عدد می باشد. |  | 1401-2294-210113 | 1401-06-13 | تعداد باتریهای نیکل کادمیوم مورد نیاز به 20 عدد از نوع H تغییر پیدا کرد. علی ایحال در زمان خرید دیزلها پیشنهاد سازنده مورد بررسی قرار خواهد گرفت شفاف سازی خواهد شد.
2 | پس از نهایی سازی محاسبه سیستم روشنایی محوطه چاهها، و اطراف فنس مربوطه ، لازم است که مدرک لیست بارها ویرزایش و در صورت نیاز توان دیزل ژنراتور بر این اساس اصلاح گردد. |  | 1401-2294-210113 | 1401-06-13 | مدرک محاسبات روشنایی تولید شده است. همچنین ظرفیت دیزل طوری در نظر گرفته شده است که امکان اضافه کردن روشنایی به آن وجود دارد. لذا میتوان این مدرک را نهایی کرد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 27-Aug-2022 |  |  |  |  | Date: