## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-DT-0004_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1284 |  |  | Transmital Date: 17-Aug-2022
Document Title: Data Sheets For Diesel Generator of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0105-EL-TR-1284 |  |  | Transmital Date: 17-Aug-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-DT-0004_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Next revision shall be issued after finalizing or minor comment on load list, Diesel generator sizing and LV switchgear single line diagram. |  | BK-SUR-ENG-ELE-00-01651 | 2021-10-02 | هر گونه تغییر در این مدرک اعمال می شود و مدرک بر اساس آن به روزرسانی میشود. |  |  | Will be checked later.
2 | This data sheet shall be rechecked with data sheet attached to IPS-M-EL-138(1) and all data which are exist in IPS data sheet shall be exist in the project data sheet. For example following items shall be added. -Weight of Exciter, Starting Equipment and etc. |  | BK-SUR-ENG-ELE-00-01651 | 2021-10-02 | بر اساس فایل ارسالی کارفرمای محترم به روز رسانی گردید. |  |  | Noted and Closed.
3 | General, Item 1.4: IPS-M-PM-290 (1), Material and Equipment Standard for Reciprocating Internal Combustion Engines shall be added as reference document. |  | BK-SUR-ENG-ELE-00-01651 | 2021-10-02 | در بند 1.2 اضافه گردید. |  |  | Noted and Closed.
4 | Generator Specification, Item 1.8: as per IPS-M-EL-138 (1) part 6.4, noise level at 1m should not normally exceed 81 dB (A) in the no load running condition. |  | BK-SUR-ENG-ELE-00-01651 | 2021-10-02 | در بند 13.1 اضافه گردید. |  |  | Noted and Closed.
5 | Generator Specification, , Item 11.10, 11.11, 11.17: The sizing shall be revised after finalizing or minor comment on diesel sizing. |  | BK-SUR-ENG-ELE-00-01651 | 2021-10-02 | بر اساس آخرین ویرایش لیست بار و محاسبات انجام شده به روزرسانی گردید. |  |  | Noted and Closed.
6 | Generator Specification, Item 11.18: According to Diesel generator specification section 4.5, Permissible overload shall be considered as below: 10% of rated current for a period of one hour (in each 12 hours function) |  | BK-SUR-ENG-ELE-00-01651 | 2021-10-02 | در بند 9.8 اعمال گردید. |  |  | Noted and Closed.
7 | Control Panel, Item 12.13, 12.17, 12.19: The protection shall be revised after finalizing or minor comments on LV switchgear single line diagram. (For example base on IPS-E-EL-100(1), there is not need to 49T and 51G, meanwhile 32 will be considered if required) |  | BK-SUR-ENG-ELE-00-01651 | 2021-10-02 | بر اساس تغییرات و کامنتها بر روی مدرک دیاگرام تک خطی کامنتها حفاظت ها در نظر گرفته شده است. همچنین به BK-SSGRL-PEDCO-110-EL-SL-0002 نیز اشاره شده است. |  |  | Noted and Closed.
8 | Switching Device, Item 13.8: Rated short circuit level shall be updated based on short circuit calculations. |  | BK-SUR-ENG-ELE-00-01651 | 2021-10-02 | در آیتم 9.21 به مدرک BK-SSGRL-PEDCO-110-EL-SL-0002 اشاره شده است. همچنین بعد از انجام محاسبات اتصال کوتاه این مدرک ویرایش می گردد. |  |  | Noted and Closed.
9 | Mechanical comment: Relevant standard for daily tank to be specified |  | BK-SUR-ENG-ELE-00-01651 | 2021-10-02 | در آیتم 4.6 به مخزن سوخت اشاره شده است. |  |  | Noted and Closed.
10 | Page 6, Items 9.17&9.18: According to basic electrical design criteria and IPS-M-EL-138(1), Insulation class and temperature rise shall be modified to "F", "B" instead of "H" and "F". |  | BK-SUR-ENG-ELE-01-04079 | 2022-04-30 | ردیف 9.17 و 9.18 اصلاح گردید. |  |  | Noted and Closed.
11 | Page 8, Item 10.15, Indicators on Panel: Indicators on local panels shall be mentioned in this document. It has not been shown on SLD. |  | BK-SUR-ENG-ELE-01-04079 | 2022-04-30 | چراغ سیگنالهای باز و بسته و خطا در این قسمت اضافه گردید. |  |  | Noted and Closed.
12 | No Comment. Note: Item 10.17: According to IPS-E-EL-100 and electrical design criteria, 50G and 64R shall be deleted. Item 9.3&9.7: Rated apparent powers shall be replaced. |  | BK-SUR-ENG-ELE-01-05532 | 2022-08-27 | مطابق با استاندارد IPS بند 7.5.3.2 صفحه 88 رله 50G و 64R برای دیزلهای کمتر از 500 کیلوولت آمپر نیاز نمی باشد. لذا در بند 10.17 حذف گردید. همچنین توانها اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 27-Aug-2022 |  |  |  |  | Date: