## CRS
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-ME-DT-0002_D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1280 |  |  | Transmital Date: 16/Aug/2022
Document Title: DATA SHEETS FOR POTABLE WATER TANK OF WELL PADS |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0105-ME-TR-1280 |  |  | Transmital Date: 16/Aug/2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-ME-DT-0002_D03 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | درخصوص ارتفاع مخزن میبایست مطابق با مقررات ملی ساختمان و محاسبات هیدرولیک جهت فشار موردنیاز به صورت ثقلی در نقطه تحویل مصرف کننده انجام پذیرد. |  | 01/2294/251971 | 1401/07/13 | فشار تحویلی در نقطه مصرف (با لحاظ نمودن مبحث 16 مقررات ملی ساختمان ) برابر با 5.5 متر ستون آب میباشد. بر مبنای آن محسابات هیدرولیک مطابق با پیوست این برگه جوابیه (شیت بعدی همین فایل اکسل) انجام شده که درنهایت ارتفاع زیر مخزن از زمین 5.5 متر بدست می آید.
2 | همانگونه که در مکاتبات پیشین مطرح گردید با توجه به مرتفع بودن مخزن، تمهیدات لازم جهت آبگیری مخزن می بایست در نظر گرفته شود. |  | 01/2294/251971 | 1401/07/13 | این مورد ارتباطی به داده برگ "مخزن آب آشامیدنی چاه ها" ندارد و نیز تامین آن در شرح کار پیمانکار نیز نمی باشد. چنانچه کارفرمای محترم بر این خواسته (فرا-قراردادی) اصرار دارد، لطفا مراتب در قابل اضافه کاری به صورت رسمی ابلاغ گردد.
توجه: با توجه به "Approved As Note" شدن مدرک در ویرایش قبلی و ارائه توضیحات تکمیلی و انجام اصلاحیه جزئی، مدرک با وضعیت AFC ارسال می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: H.Adineh | Signature | M.Fakharian
| Date: |  |  |  |  | Date:

## Hyd. Calc. For Tank EL.
SERVICE : POTABLE WATER |  |  | TO: USER |  |  |  |  | Line Loss(ΔP)=
FLUID :WATER
PROCESS DATA
|  |  | SP. GR. |  |  |  | 1
STD MASS DENSITY (KG/M3) | (KG/M3) | 1000 | NORMAL MASS FLOW KG/HR |  |  |  | 100 | Line Loss(Suction)
TEMP. | °C | AMB | FLOW RATE (NORMAL) (@ P,T) M3/HR |  |  |  | 0.1
VISCOSITY (@ P,T) | CP | 1.6 | FLOW RATE (RATED) (@ P,T) M3/HR |  |  |  | 0.11 | Flow Rate m3/hr | Out D(in) | f | Inner D(in) | r (kg/m3) | V(m/s) | ΔP (bar/km) | L(m) | ΔP(bar)
TRUE VAPOR PRESSURE@OPERATING T. | BARA | 0.1 | FLOW RATE (MINIMUM) (@ P,T) M3/HR |  |  |  | 0.03
USER DELIVERY PRESSURE |  |  | LOSS IN VALVE & FITTING (SUCTION) |  |  |  |  | 0.1 | 2 | 0.091954 | 1.2504 | 1000 | 0.035063 | 0.017797 | 20 | 0.00035595
ORIGINAL PRESS | BARA | 1.013 |  | TYPE | QTY | L/D | LOSS(Bar)
± STATIC HD (M×SG/10.21) | BAR | 0.52889 | 1 | VALVE | 2 | 20 | 2.261e-05 | Elevation @ Bottom of Tank | [6 empty] | M | 5.3
-LOSS (LINE+OTHERS) | BAR | -0.00047182 |  | CHECK | 0 | 135 | 0 | Low Low Liquid Level | [6 empty] | M | 0.1
USER DELIVERY PRESSURE | BAR | 1.5414 |  | TEE | 3 | 30 | 5.0872e-05 | AVAILABLE NPSH (m) |  |  | #REF! | Discharge Pressure (barg) |  |  | #REF!
USER DELIVERY PRESS | M | 5.5279 |  | ELBOW | 3 | 25 | 4.2393e-05
|  |  |  | Fitting Equivalent Length (m) |  |  | 6.5108
توجه: مطابق با مبحث 16 مقررات ملی ساختمان، فشار پشت شیر مصرف کننده میبایست 5.5 متر (ستون آب) باشد.
1
Viscosity (cp) |  | 1.6
Density (kg/m3)) |  | 1000
ε (mm) |  | 0.045
Diameter (m) |  | 0.03176
Area of Pipe (m2) |  | 0.00079223
Velocity (m/sec) |  | 0.035063
Rated Mass Flow (kg/hr) |  | 100
Rated Constant |  | 1
Normal mass Flow (kg/hr) |  | 100
Volume Flow (m3/hr) |  | 0.1
Re |  | 695.9966
ε/D |  | 0.0014169
f |  | 0.091954
-4.1195
16.9703
Outlet Diameter, mm |  | 50.8
Thickness,mm |  | 9.52
Inner Diameter,mm |  | 31.76
30