## Sheet 1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-SA-PF-0001_D00 |  |  |  |  | EPC Contractor Tr. No : BK-HD-PEDCO-T-0333 |  |  | Transmital Date:13/DEC/2021
Document Title: PFD - Fire Water System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-SF-TR-0333 |  |  | Transmital Date:13/DEC/2021
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-SA-PF-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | جهت خروجی Relief Valve پمپ دیزل و PCV بر روی هدر (درصورت نیاز به نصب بر اساس استاندارد)، خط برگشت به مخزن (Recycle) لحاظ شود. |  | 1400-2294-345121 | 1400/10/12 | جهت خروجی Relief Valve پمپ دیزل، خط برگشت به مخزن اضافه گردید ( قبلا در مدرک P&ID در نظر گرفته شده بود). مطابق استاندارد NFPA 20 نیازی به در نظر گرفتن PCVبر روی هدر نمی باشد.
2 | جهت پر کردن مخزن پمپ پر کن لحاظ شود. |  | 1400-2294-345121 | 1400/10/12 | اتصال مربوطه جهت پر کردن مخزن توسط تانکر در نظر گرفته شد. لازم به ذکر است با توجه به نبود پمپ پر کن در شرح خدمت پیمان و مدارک مهندسی Basic، موضوع اضافه شدن این پمپ پس از تایید اضافه کاری در مدرک لحاظ خواهد شد.
3 | جهت پر کردن مخازن، اتصلات مربوط به پر کردن از طریق خودرو تانکر و آب پایدار لحاظ گردد. |  | 1400-2294-345121 | 1400/10/12 | اتصال مربوطه جهت پر کردن توسط تانکر در نظر گرفته شد. لازم به ذکر است این مورد با لحاظ نمودن اضافه کاری موضوع، در مدرک حاضر لحاظ گردید.
4 | لازم است حجم مخزن بعد از نهایی شدن محاسبات Demand در مدرک ذکر گردد. |  | 1400-2294-345121 | 1400/10/12 | با توجه به آخرین ویرایش مدرک Fire water demand j ارسال شده حجم مورد نیاز مخزن در مدرک لحاظ گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: