## Sheet 1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-SA-PI-0001_D01 |  |  |  |  | EPC Contractor Tr. No : BK-HD-PEDCO-T-0985 |  |  | Transmital Date:22/MAY/2022
Document Title: P&ID - Fire Water Network |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-SF-TR-0985 |  |  | Transmital Date:22/MAY/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-SA-PI-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | یک عدد PG در مجاورت PT-2301 در نظر گرفته شود. |  | 1401-2294-165031 | 1401/05/11 | در نظر گرفته شد.
2 | برای پمپ ها Selector جهت Auto/Manual در نظر گرفته شود (شماتیک نشان داده شده اصلاح شود و سیمبل مناسب جهت سلکتور تعریف گردد)، همچنین فیدبک ارسالی به F&G اصلاح شود |  | 1401-2294-165031 | 1401/05/11 | اصلاح گردد.
3 | مسیز sensing فشار خروجی پمپ ها و ادوات نصب شده مطابق استاندارد NFPA اصلاح گردد. |  | 1401-2294-165031 | 1401/05/11 | مسیر sensing فشار خروجی پمپ ها و ادوات نصب شده بر اساس NFPA 20 بین چک ولو تخلیه پمپ و Isolation valve در نظر گرفته شده است.
4 | مطابق با شماتیک نشان داده شده برای پمپ دیزل و قرار دادن PSL: چگونه Note های شماره 24 و 23 جهت تشخیص 5 بار و 10 بار محقق می گردد؟ لازم است مطابق NFPAاصلاح گردد. |  | 1401-2294-165031 | 1401/05/11 | اصلاح گردید.
5 | شایان ذکر است در صورت حذف Storage Tank، لازم است مدرک مورد بازنگری قرار گیرد و جهت بررسی مجدد به این امور ارسال گردد. |  | 1401-2294-165031 | 1401/05/11 | ویرایش جدید مدرک بر اساس آخرین تغییرات مورد بازنگری قرار گرفت و Storage Tank حذف گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: