## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0028_D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1520 |  |  | Transmital Date: 19/Oct/2022
Document Title: Mechanical Data Sheets For Fire Water Jockey Pumps |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-ME-TR-1520 |  |  | Transmital Date: 19/Oct/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-ME-DT-00280_D03 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به كلاس خط - #150 - ، كلاس فلنج ها به #250 تغيير داده شود. |  | BK-SUR-ENG-MEC-01-06042 | 2022-10-31 | Noted
Electrical comments :
1 | پيرو مذاكره با كارشناس برق مشاور با توجه به اينكه مطابق با استاندارهاي IPS-M-PM-125 و NFPA20، ظرفيت 150 درصد بر روي BHP اعمال خواهد شد و سپس جهت استفاده در مدرك لود ليست برق در اختيار بخش برق مشاور قرار خواهد گرفت، لذا نوت 24 ميبايست حذف گردد. |  | BK-SUR-ENG-MEC-01-06042 | 2022-10-31 | Noted
2 | در بخش مربوط به General Note، نوت زير اضافه گردد. "Electrical motor shall be rated according to project site condition" |  | BK-SUR-ENG-MEC-01-06042 | 2022-10-31 | Noted
3 | تغييرات مجاز ولتاژ و فركانس در صفحه 5 ديتا شيت، مطابق با مدرك ديتا شيت برقي توسط مشاور بررسي و اصلاح گردد |  | BK-SUR-ENG-MEC-01-06042 | 2022-10-31 | As per clause 7.1.6 of IPS-M-EL-131 voltage variation of ±5% is acceptable.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: H. Adineh | Signature | M. Fakharian
| Date: 10/31/2022 |  |  |  |  | Date: 11/06/2022