## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-PEDCO-120-PR-DT-0003 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1252 |  |  | Transmital Date: 8/6/2022
Document Title:Process Data Sheets For 1st Stage Gas Air Coolers |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-1252 |  |  | Transmital Date: 8/6/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-PR-DT-0003_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | كامنت پيشين: پاسخ پيمانكار قانع كننده نبوده و لازم است محاسبات ترمال براي كولر ارائه گردد. |  | BK-SUR-ENG-PCS-01-05481 | 2022-08-20 | اعمال گردید.
2 | كامنت پيشين: پاسخ پيمانكار قانع كننده نبوده و لازم است بر اساس محاسبات ، سطح اوليه مي بايست مشخص گردد. |  | BK-SUR-ENG-PCS-01-05481 | 2022-08-20 | اعمال گردید.
3 | كامنت پيشين: پاسخ پيمانكار قانع كننده نبوده و لازم است تعداد Bay, Boundle و ساير موارد مشخص گردد. |  | BK-SUR-ENG-PCS-01-05481 | 2022-08-20 | اعمال گردید.
4 | كامنت پيشين: پاسخ پيمانكار قانع كننده نبوده و لازم است ميزان بار الكتريكي موتور ها و تعداد آن مشخص گردد. |  | BK-SUR-ENG-PCS-01-05481 | 2022-08-20 | اعمال گردید.
5 | كامنت پيشين: پاسخ پيمانكار قانع كننده نبوده و لازم است موارد مورد درخواست از سازنده همچون سويچ هاي لرزش در مدرك مشخص گردد. |  | BK-SUR-ENG-PCS-01-05481 | 2022-08-20 | سوییچ های لرزشی در مدارک سازنده اعمال خواهد شد.
6 | مدرك ‍Criteria و اسناندارد IPS-E-PR-785 به عنوان مرجع ذكر گردد |  | BK-SUR-ENG-PCS-01-05481 | 2022-08-20 | اعمال گردید.
7 | حداكثر دماي هواي خروجي مجاز، مطابق بند 8.3.3 استاندارد فوق در مدرك لحاظ گردد. |  | BK-SUR-ENG-PCS-01-05481 | 2022-08-20 | پیرو مذاکرات شفاهی دما خروجی برابر با 70 درجه سانتیگراد در نظر گرفته شد.
8 | ضروريست نقطه نظرات ذينفع اصلي در خصوص اين مدرك اعمال گردد. |  | BK-SUR-ENG-PCS-01-05481 | 2022-08-20 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: 24/08/2021