## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
PROCESS DATA SHEETS OF DIESEL PUMP
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 3
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | PR | DT | 0029 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
PROCESS DATA SHEETS OF DIESEL PUMP نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | OCT.2022 |  | IFA |  |  |  | M.Aryafar |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | AUG.2022 |  | IFA |  |  |  | M.Aryafar |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | FEB.2022 |  | IFC |  |  |  | M.Aryafar |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | JAN.2022 |  | IFC |  |  |  | M.Aryafar |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: |  |  |  | F0Z-708773
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
PROCESS DATA SHEETS OF DIESEL PUMP
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 3
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | PR | DT | 0029 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | X |  | X |  |  |  | 67
4 | [8 empty] | 68
5 | [8 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Sheet 1
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
PROCESS DATA SHEETS OF DIESEL PUMP
شماره پیمان: | [5 empty] | پروژه | بسته کاری |  | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه |  |  | شماره صفحه: 3 از 3
9184 – 073 - 053 | [5 empty] | BK | GCS |  | PEDCO | 120 |  | PR |  | DT |  | 0029 |  |  | D03
1 | Note | [23 empty] | Rev
2 |  | GENERAL DATA
3 |  | Type
4 |  |  | Centrifugal |  | Positive displacement
5 |  | Centrifugal |  |  | Horizontal |  |  |  |  | Vertical
6 |  | Positive displacement |  |  | Reciprocating |  |  |  |  | Rotary | [5 empty] | Metering
7 |  | Item |  | P-2206 | [5 empty] | No. of Main/Stand By Units | [6 empty] | 1 / 0 | [7 empty] | D03
8 |  | Service |  | Diesel Pump | [5 empty] | Installation (Indoor-Outdoor-Other) | [7 empty] | Outdoor
9 |  | Operation |  |  | Continuous |  |  |  |  | Discontinuous | [5 empty] | Parallel |  |  |  | Single
10 |  | Type of Driver | [8 empty] | Electrical Motor
11 |  | CHARACTERISTICS OF HANDLED LIQUID
12 |  | Type of Handled Liquid | [11 empty] | Diesel Fuel Oil
13 |  | Pumping Temp.e (Min. / Max.) | [5 empty] | °C | [6 empty] | 5 | / | 50
14 |  | Density at Min. / Norm / Max. Temp. | [5 empty] | kg/m³ | [5 empty] | / | 850 |  |  |  | /
15 |  | Viscosity At Min. / Normal / Max. Temp. | [5 empty] | cP | [5 empty] | / | 4.8 |  |  |  | /
16 |  | Vapour Pressure at Max. Pumping Temp. | [5 empty] | bara | [6 empty] | Negligible
17 |  | Freezing Point / Pour Point | [5 empty] | °C
18 |  | Dissolved Gas | [5 empty] | Yes-No | [6 empty] | No
19 |  | Corrosive / Erosive / Hazardous Agents / Flammable | [5 empty] | Yes-No |  |  |  |  | No | / | No | / | No | / | Yes
20 |  | Suspended solids (Type / Dimen. / Vol.%) | [5 empty] | mm | [5 empty] | / |  |  |  |  | /
21 |  | OPERATING CONDITIONS
22 |  | Suction Pressure (Min/ Max.) | [5 empty] | barg | [6 empty] | 0 |  |  |  | / | 0.11
23 |  | Discharge Pressure at Rated Capacity | [5 empty] | barg | [7 empty] | 0.95
24 |  | Differential Pressure at Rated Capacity | [5 empty] | bar | [7 empty] | 2 | [8 empty] | D03
5 |  | Capacity (Min. / Normal / Rated) | [5 empty] | m3/hr | [5 empty] | / | 5 |  |  |  | / | 5.5+MinFlow |  |  |  | Note 1 , 2
6 |  | Head at Rated Capacity | [5 empty] | m | [7 empty] | 24 | [8 empty] | D03
7 |  | NPSH Available | [5 empty] | m | [7 empty] | 10
8 |  | Max Allowable Pressure at Shut-Off | [5 empty] | barg | [7 empty] | 2.1
9 |  | Hydraulic Power | [5 empty] | kW | [7 empty] | 0.3 | [8 empty] | D03
10 |  | Reacceleration | [5 empty] | Yes-No | [7 empty] | No
11 |  | Automatic Start-Up | [5 empty] | Yes-No | [7 empty] | No
12 |  | Start-Up with Delivery Valve |  |  | Open |  |  |  |  | Close
13 |  | Flow Controlled By |  |  | Pressure Controller |  |  |  |  | Level Controller | [5 empty] | Flow Controller |  |  |  |  | Other
14 |  | DESIGN CONDITIONS
15 |  | Design Temperature: Min / Max | [5 empty] | °C | [6 empty] | 5 |  | / | 85
16 |  | Design Pressure | [5 empty] | barg | [7 empty] | 2.1
17 |  | MECHANICAL DATA
18 |  | Contamination of Liquid Handled Allowed | [5 empty] | Yes-No | [7 empty] | No
19 |  | Air Entrainment Allowed | [5 empty] | Yes-No | [7 empty] | No
20 |  | Leaks Allowed | [5 empty] | Yes-No | [7 empty] | Yes
21 |  | Antifreezing Protection | [5 empty] | Yes-No | [7 empty] | No
22 |  | Suction Line: Diameter | [5 empty] | in | [7 empty] | 2"
23 |  | Discharge Line: Diameter | [5 empty] | in | [7 empty] | 2"
24 |  | Mat. in Contact with Liq. Handled (Min.) | [10 empty] | (API 610 Cl. S-1) | [9 empty] | Note 5
25 | Note
26 | 1 |  | Design (rated) flow rates is 110 % of normal flow rate.
27 | 2 |  | Due to continous minimum flow line by orifice, Pump rated flow = Rated process flow (5.5 m3/hr) + Pump min flow.
28 | 3 |  | Deleted
29 | 4 |  | API Plan 11 shall be considered. (Vendor to confirm)
30 | 5 |  | (Vendor to confirm)
31 | 7 |  | Margin between NPSHA and NPSHR shall not be less than 1 m.
32 | 8 |  | Applicable standards are: ISO 5199, IPS-M-PM-115
33 | 9 |  | Refer to hazardous area classification layout, all instrumentation and electrical devices shall be suitable for: safe area
34 | 10 |  | Deleted | [21 empty] | D02
35 | 11 |  | For P&ID refer to BK-GCS-PEDCO-120-PR-PI-0023
36 | 12 |  | Minimum Design Metal Tep (MDMT) = 5
This document is the sole property of NISOC and all information contained herein may neither be reproduced, used, disclosed, transmitted nor in any way made public without permission of the CLIENT.