## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0011_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0377 |  |  | Transmital Date: 25/DEC/2021
Document Title:Mechanical Data Sheets For Elevated Potable Water Tank |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0009-ME-TR-0377 |  |  | Transmital Date: 25/DEC/2021
[5 empty] | CRS No:NISOC-CRS-BK-GCS-PEDCO-120-ME-DT-0011_D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به اینکه محاسبات طراحی ارسال نشده است، ضروری است معیار تعیین حداقل ضخامتها در مدرک مشخص گردد. در ضمن چنانچه در این زمینه محاسبات اولیه صورت گرفته است ارایه آن ضرورت دارد. |  | 00/22/2294/347297 | 1400/10/13 | اطلاعات مربوط به ضخامت قسمت های مختلف تانک از مدرک مذکور حذف گردید.
2 | الزام سازنده به ارایه کتابچه محاسبات و مدارک طراحی به عنوان یادداشت ذکر گردد. |  | 00/22/2294/347297 | 1400/10/13 | .(Note 26) مطابق نظر کارفرمای محرم اصلاح گردید
3 | درج کالای یدکی در این مدرک و قراردادن آن در تعهد سازنده مخزن، مقبولیت ندارد. می بایست اقلام یدکی در دیگر مدارک مرتبط لحاظ گردد. |  | 00/22/2294/347297 | 1400/10/13 | نظرات کارفرمای محترم اعمال شد.
4 | شرایط محیطی منطبق با دمای زیر آفتاب 85درجه، در سایه 55 درجه و رطوبت 100 درصد در نظر گرفته شده و در مدارک اعلام گردد. |  | 00/22/2294/327356 | 1400/09/29 | مطابق نامه شماره 00/2294/342083 به تاریخ 1400/10/09 کارفرمای محترم بر مدارک داده برگ های فنی فرآیند دمای طراحی 85 درجه سانتیگراد و دمای محیط کمترین 5 درجه و بیشترین دما 50 درجه سانتیگراد اعلام شده است.
5 | اطلاعات ابزاردقیقی و کنترلی در data sheet های ارایه شده قید گردیده و در قالب note به spec های مربوطه ارجاع شوند. |  | 00/22/2294/327356 | 1400/09/29 | اطلاعات مربوط به بخش ابزار دقیق در note 18 مشخص شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.BAVARSAD | Signature | H.naserizadeh |  |  | Clarified By: H.Ghadyani | Signature | M.Fakharian
Date:12/15/2021