## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-PEDCO-120-ME-DT-0017-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1095 |  |  | Transmital Date: 19/June/2022
Document Title: Mechanical Data Sheets For Fire Water Storage Tank |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0010-ME-TR-1095 |  |  | Transmital Date:19/June/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-ME-DT-0017-D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بند شماره 11 یادداشتها با استاندارد مرجع مغايرت دارد كه مي بايست اصلاح گردد. |  | 01/2294/175140 | 1401/05/22 | بند شماره 11 جزء ایتم های بولت دار می باشد و ملزم به رعایت بند قرارداد نمی باشد.
2 | بخش اشاره شده در 12 یادداشتها با آخرين ويرايش استاندارد IPS مطابقت ندارد. |  | 01/2294/175140 | 1401/05/22 | یادداشت مورد نظر در زمان ساخت تجهیز بدر نقشه های ساخت نهایی می گردد.
3 | ظرفيت مخزن با اطلاعات مندرج در اسناد پايه مغايرت دارد. |  | 01/2294/175140 | 1401/05/22 | بر اساس مدرک FIRE WATER CALC. DEMAND که اخیرا به تایید آن کارفرمای محترم رسیده است، ظرفیت مخزن تغییر کرده است.
4 | میزان خوردگی مجاز پس از نهایی شدن مطالعات خوردگی قابل استناد خواهد بود. |  | 01/2294/175140 | 1401/05/22 | مطالعات خوردگی مربوطه پیش تر تایید شده و نسخه AFD آن نیز طی ترانسمیتال 1228 ارسال شده است
5 | ماکزیمم قطر و ارتفاع مخزن با اطلاعات مندرج در استناد پایه مغایرت دارد. |  | 01/2294/175140 | 1401/05/22 | قطر و ارتفاع مخزن بر اساس مدرک FIRE WATER CALC. DEMAND که اخیرا به تایید آن کارفرمای محترم رسیده است، مشخصات قطر و ارتفاع تغییر کرده است.
6 | مبنای درج پیش آمدگی نازلهای مخزن مشخص گردد. |  | 01/2294/175140 | 1401/05/22 | جهت جلوگیری از ایجاد دفرمگی و آسیب دیدن ورق های بدنه و ورق کف نازلهای ورودی به مخزن که در ارتفاع بالای بدنه نصب میشود را با پیش آمدگی در نظر می گیرند و مقدار پیش آمدگی در نقشه ساخت سازنده مطابق STANDARD DRAWING ها اجراء خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Bavarsad | Signature | H.Naserizadeh |  |  | Clarified By: H.Ghadyani | Signature | M.Fakharian
| Date: 9/4/2022 |  |  |  |  | Date: