## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0011-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0377 |  |  | Transmital Date: 25/Dec/2021
Document Title: Mechanical Data Sheets For Elevated Potable Water Tank |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0010-ME-TR-0377 |  |  | Transmital Date: 25/Dec/2021
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-BK-GCS-PEDCO-320-ME-DT-0011-D01 |  |  | CRS Status: | C3
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Note 7: discrepancy with 8mm thickness specified in the drawing and datasheet |  | BK-SUR-ENG-MEC-00-03338 | 2022-03-05 | Noted.
2 | Prior to finalization of P&ID, this datasheet can not be approved. |  | BK-SUR-ENG-MEC-00-03338 | 2022-03-05 | This document is prepared based on Process data sheet.
3 | For blasting Galv. surfaces special procedure shall be included in the BK-GENRAL-PEDCO-000-PI-SP-0006 |  | BK-SUR-ENG-MEC-00-03338 | 2022-03-05 | This specification has been approved and changing on it would not be approved by NISOC. Based on IPS-E-TP-100 standard, hot dip galvanized coating shall be carried out according to BS 729. So surface preparation will be reffered to this standard as per Note 11.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Bavarsad | Signature | H.naserizadeh |  |  | Clarified By: | Signature
Date: 3/5/2022